## Risk Matrix 1
Risk Assessment Matrix
Impact
Impact area | 1 - Minimal | 2 - Minor | 3 - Moderate | 4 - Major | 5 - Catastrophic
Safety/ Environment | Minor Safety event with the potential to cause up to 20 minor injuries or a single major injury and with environmental incidents that can be addressed using existing control measures | Significant Safety event with the potential of a single major injury to five major injuries with adverse environmental impact within a control period that can be mitigated using existing control measures | Significant safety event with the potential of between five major injuries and two fatalities, with significant environmental impact that results in Regulatory intervention and it exceeds existing control measures | Catastrophic Safety event with the potential of between two and 10 fatalities, with major environmental impact resulting in Regulatory fines and current control measures are not suitable | Catastrophic Safety event with the potential of over 10 fatalities, with catastrophic long term environmental damage
Performance | Planned disruption for up to a day on any one Route | Unplanned disruption for up to day on any one Route | Unplanned disruption (for up to a week) on any one route or multiple routes | Unplanned disruption for over a week on multiple Routes | Prolonged and unplanned severe disruption to key routes resulting in adverse media attention and protests/lobbying resulting in a review of Network licence condition
Finance | Costs to resolve issue - up to £2m per annum | Costs to resolve issue - £2m to £25m per annum | Costs to resolve issue - £25m - £75m per annum | Costs to resolve issue - £75m to £250m per annum | Costs to resolve issue in excess of £250m per annum
Likelihood
| 1 - Highly Unlikely | 2 - Unlikely | 3 - Possible | 4 - Likely | 5 - Almost certain
Likelihood criteria | No known event or if known extremely rare | Low likelihood the risk will occur and current mitigations provide effective risk control | Medium likelihood with risks resolved using current controls. Further control improvements underway or actively being developed to mitigate | High likelihood the risk will occur with current controls ineffective leaving problem unresolved for a long period. No effective mitigations currently identified and control weakness known and unmanaged | Very High likelihood the risk will occur and there are no effective controls or mitigations to prevent the event
Impact: Risk score = Impact x Likelihood
Likelihood | Minimal | Minor | Moderate | Major | Catastrophic
Almost Certain | 5 / moderate | 10 / major | 15 / major | 20 / severe | 25 / severe
Likely | 4 / moderate | 8 / moderate | 12 / major | 16 / major | 20 / severe
Possible | 3 / minor | 6 / moderate | 9 / moderate | 12 / major | 15 / major
Unlikely | 2 / minor | 4 / moderate | 6 / moderate | 8 / moderate | 10 / major
Highly Unlikely | 1 / minor | 2 / minor | 3 / minor | 4 / moderate | 5 / moderate

## Data (hidden)
Risk Assessment
Function | Climate Variable | Type of risk | Location | Function Type is company specific - examples below - needs more thought
Select option | Select option | Select option | Select option | Function Type - Network Rail | Function Type - TfL
Service | Extreme hot days | Direct | Coastal | Buildings | Ground (e.g. drought causing fissures in clay)
Asset | Heat wave | Indirect | Highlands | Drainage | Tracks
| Higher average temperature | Cumulative | Lowlands | Geotechnics | Tunnels
| Snow | Interdependency (us on us) | Underground | Lineside | Bridges & viaducts
| Ice/Hail | Interdependency (us on them) | Sub surface | Mining and Tunnels | Embankments & cuttings
| Snow/ice | Interdependency (them on us) | Overground | Plant | Drainage
| Large diurnal temperature range |  | South West | Power and Electrical | Power supply (non-rail infrastructure)
| Long hot, dry summer |  | South East | Signalling | Sub-stations
| Long wet winter/spring |  | Midlands and Anglia | Structures | Third rail systems
| Heavy rain/cloudburst |  | Wales | Switches and Crossings | Overhead line electrification
| Light rain/drizzle |  | Northern England | Telecoms | Signalling systems
| High average rainfall over several days |  | Southern Scotland | Track | Comms systems
| High average rainfall over season |  | Northern Scotland | etc…………………… | Control centres
| Low average rainfall |  | Whole country |  | Depots
| High soil moisture |  |  |  | Rolling stock
| Low soil moisture |  |  |  | Maintenance staff and equipment
| Flooding |  |  |  | Station assets (approaches, signs, lifts, PA, interchanges, etc.)
| Erosion |  |  |  | Green assets (trees, other vegetation)
| Lightning |  |  |  | Boundary issues (e.g. on-street running of trams, level crossings)
| High winds |  |  |  | People (passengers and staff)
Storms
Note on B3: Lisa Constable: Have just brainstormed ideas, this is too long and some of the items are a consequence of the others so needs more thinking

## Risk Assessments
Risk Assessment
Ref. | Function | Function Type | Asset (from asset accountability matrix) | Climate Variable | Type of risk | Risk | Location | Risk owner | Decision threshold, process or trigger point for action on the risk | Narrative | ARP 3 risk current score (as of 2019) | Confidence (high /medium/ low) for 2019 | Narrative | Risk scores for 2050s (assuming no additional adaptation) | Risk scores for 2080s (assuming no additional adaptation) | Confidence (high/ medium/ low) | Narrative | Assumptions (including on data, operational, regulatory changes, etc) | Linked CCRA3 Risks
AP1 | Asset | Access Point | All access point types | Heavy rain/cloudburst | Interdependency (us on them) | Earthwork failure due to heavy rain, causing access facility to fail, e.g. movement of access steps/handrail | Whole country | Professional Head of Geotechnical | Increased risk of trespass and closure of access point until maintenance or renewal undertaken. | There are links to earthwork failure/potential bank slip where an access point can be affected due to slippage e.g. steps/ handrail. Leads to performance and safety issues due to inability to access the railway/taking longer to attend an incident as staff may need to walk further to site/incident | 6/moderate | Medium | Heavy rainfall could destabilise the earthwork causing the land to slip. If this is near an access facility (e.g. a set of steps leading to the track a landslip could cause the whole access facility to slip | 9/moderate | 9/moderate | Low | In the absence of any change to earthworks standards and regimes, the risk will increase. If earthworks standards are revised to account for climate change the level of risk and frequency of events could remain the same as current | Assuming earthworks standards remain as current, the risk impact should remain the same but the likelihood will increase | Risks to infrastructure services from river, surface water and groundwater flooding | Risks to transport networks from slope and embankment failure
AP2 | Asset | Access Point | All access point types | Flooding | Direct | All sources of flooding leading to pooling of water causing wet ground conditions (e.g. heavy rainfall, river flooding, etc) resulting in inaccessibility in and out of access facilities due to vehicles becoming stuck, and reduced stability of parts of the asset, e.g. steps, | Whole country | Professional Head of Drainage and Off Track | Increased risk of trespass and closure of access point until maintenance or renewal undertaken. | Flooding may also be linked to the drainage asset due to blockages in the drainage system causing water to overflow and waterlogging which could affect the stability of the access point in particular access points on an embankment/cutting? Leads to performance and safety issues due to inability to access the railway/taking longer to attend an incident as staff may need to walk further to site/incident | 1/minor | Medium | The risk of an incident occurring at an access point due to heavy rainfall is minimal, however failure of an access point can have an affect on safety and performance | 2/minor | 2/minor | Low | If we carry on undertaking more frequent inspections, more regular maintenance or renewal of assets more prone to failure at the current level the risk impact should not increase but the likelihood will go up | The future climate projections suggests storm events will be more frequent, this could mean that it will be more likely for heavy rain and flooding events, better drainage at access points will be beneficial | Risks to infrastructure services from river, surface water and groundwater flooding
BD1 | Asset | Boundary | All fence types | Heavy rain/cloudburst | Direct | Pooling of water causing wet ground conditions resulting in movement of fence posts especially where land is sloping down toward the railway | Whole country | Professional Head of Drainage and Off Track | Increased risk of incursion both livestock and people Inspection resulting in maintenance or renewal required | Heavy rainfall resulting in flooding may also be linked to the drainage asset due to blockages in the drainage system causing water to overflow and waterlogging which could affect the stability of the boundary? Flooding may also be caused by third parties such as rivers bursting their banks or overflow of other water bodies | 6/moderate | Medium | Wet ground conditions are known to have an effect on the stability of fence posts. This may be dependent on the depth of the footings, materials used and age of fence. Although this would be classed as an unlikely event, this type of issue has been known to occur on the infrastructure | 9/moderate | 9/moderate | Low | If we carry on undertaking inspection, maintenance and renewal at the current level the impact should not change although enhanced inspections may be required with more frequent repairs due to an increase in likelihood of damage | The future climate suggests storm events will be more frequent, this could mean that poor ground conditions will be more likely in some locations with sloping ground resulting in a higher level of maintenance/increased inspections | Risks to infrastructure services from river, surface water and groundwater flooding | Risks to transport networks from slope and embankment failure
BD2 | Asset | Boundary | Wall | Storms/high winds | Direct | High winds causing trees to fall onto wall resulting in damage and loss of effective boundary | Whole country | Professional Head of Drainage and Off Track | Increased risk of incursion both livestock and people Inspection resulting in maintenance or renewal required | A NR/3rd party Tree falling onto a boundary/dry stone wall, has the potential to create loss of boundary, there is also the risk of the wall falling onto a person and/or 3rd party property. Vegetation management may be required for NR trees and liaison with adjacent land owners for 3rd party trees. Boundary repair/renewal will be required | 6/moderate | Medium | Although this would be classed as an unlikely event the loss of boundary in particular where there is livestock could result in a train derailment | 9/moderate | 9/moderate | Low | If we carry on undertaking inspection, maintenance and renewal at the current level the impact should not increase, although enhanced inspections may be required with more frequent repairs due to an increase in likelihood of damage | The future climate suggests storm events will be more frequent, this could mean that it will be more likely for trees to fall over, however with vegetation management, identification of problem trees and continued inspection this will reduce the increase in risk | Risk to transport from high and low temperatures, high winds, lightning | Risk to transport from high and low temperatures, high winds, lightning
BD3 | Asset | Boundary | All fence types | Storms/high winds | Direct | High winds causing trees to fall onto fencing resulting in damage and loss of effective boundary | Whole country | Professional Head of Drainage and Off Track | Increased risk of incursion both livestock and people Inspection resulting in maintenance or renewal required | A NR/3rd party Tree falling onto a boundary/dry stone wall, has the potential to create loss of boundary, there is also the risk of the wall falling onto a person and/or 3rd party property. Vegetation management may be required for NR trees and liaison with adjacent land owners for 3rd party trees. Boundary repair/renewal will be required | 6/moderate | Medium | Although this would be classed as an unlikely event the loss of boundary in particular where there is livestock could result in a train derailment | 10/major | 10/major | Low | If we carry on undertaking inspection, maintenance and renewal at the current level impact should not increase, although enhanced inspections may be required with more frequent repairs due to an increase in likelihood of damage | The future climate suggests storm events will be more frequent, this could mean that it will be more likely for trees to fall over, however with vegetation management, identification of problem trees and continued inspection this will reduce the increase in risk | Risk to transport from high and low temperatures, high winds, lightning
BD4 | Asset | Boundary | Wooden panel | High winds | Direct | Wind loading causing fence to lean/fall over, resulting in the loss of an effective boundary | Whole country | Professional Head of Drainage and Off Track | Increased risk of incursion both livestock and people Maintenance, or renewal required. Upgrade of fence type may be required if in an area more susceptible to high winds | Maintenance or renewal will be required in the event of a loss of boundary incursion due to high winds. Temporary measures and/or increased inspection may be required until works are undertaken | 6/moderate | Medium | Wooden panel fencing is usually in residential areas, therefore the risk of livestock incursion is reduced/minimal. Which reduces the impact | 9/moderate | 9/moderate | Low | If we carry on undertaking inspection, maintenance and renewal at the current level impact should not increase, although enhanced inspections may be required with more frequent repairs due to an increase in likelihood of damage | The future climate suggests that high winds will be more prevalent. Assumption that current management practices will continue | Risk to transport from high and low temperatures, high winds, lightning
BD5 | Asset | Boundary | All fence types | Heavy snow | Direct | Snow loading causing fence to lean/fall over, resulting in the loss of an effective boundary | Localised | Professional Head of Drainage and Off Track | Increased risk of incursion both livestock and people. Maintenance or renewal required | Maintenance or renewal will be required in the event of a loss of boundary incursion due to heavy Snow. Temporary measures and/or increased inspection may be required until works are undertaken | 6/moderate | Medium | Heavy snow and drifting is more likely in certain areas such as higher ground, so this may not be a high risk everywhere | 4/moderate | 4/moderate | Low | If we carry on undertaking inspection, maintenance and renewal at the current level the risk should not increase, but likelihood is likely to reduce | The future climate suggests that occurrences of heavy snow will reduce in the future. Therefore reducing the risk of boundary failure due to snow | Risk to transport from high and low temperatures, high winds, lightning
BD6 | Asset | Boundary | All fence types | Heavy rain/cloudburst | Interdependency (us on them) | Earthwork failure due to heavy rain, causing boundary to fail | Whole country | Professional Head of Geotechnical | Increased risk of incursion both livestock and people. Maintenance or renewal required | There are links to earthwork failure/potential bank slip where the boundary at the bottom or top of the embankment could be at risk | 6/moderate | Medium | Heavy rainfall could destabilise the earthwork causing the land to slip, this in turn could bring fencing down, causing a failure of the boundary measure and result in livestock incursion/trespass | 9/moderate | 9/moderate | Low | Dependent on future earthworks programme and development | Dependent on future earthworks programme and development of more resilient embankments or cuttings this risk impact should remain the same but the likelihood will increase | Risks to infrastructure services from river, surface water and groundwater flooding | Risks to transport networks from slope and embankment failure
DR1 | Asset | Drainage | Culvert | Heavy rain/cloudburst | Direct | Design capacity of culvert exceeded and system surcharges with potential for resulting damage to surrounding earthwork and or flooding track | Whole country | Professional Head of Drainage and Off Track and Professional Head of Geotechnical | Linked to trigger level for investment which is asset condition or need to uprate culvert size/capacity | There is a risk across the country although there may be a higher risk in the North West and areas where rainfall levels are projected to increase further than in the south. | 9/moderate | Medium | Current asset condition and location knowledge is limited. Work over next three years focusses on providing better data | 12/major | 16/major | Low | Increasing intense rainfall and lack of investment in drainage assets will increase the risk of failure in the future | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
DR10 | Asset | Drainage | Underground piped drainage | High soil moisture | Direct | Soil swelling during wetter weather and usually after a period of hotter drier summers and consequent soil shrinkage could result in misalignment of pipes and collapse of already damaged pipes and culverts with a resultant reduction in performance | Whole country | Professional Head of Drainage and Off Track | Linked to trigger level for investment which is asset condition/ drainage failing to function as designed for NR managed assets/ flood events for third party lineside neighbour assets | More extreme wetting of soils has the potential to increase movement resulting from swelling of soils. Open jointed or damaged pipes and culverts may be compromised in terms of their ability to manage flows | 3/minor | Low | Up to date condition data on an asset that is buried is difficult to ascertain. Damage may not be apparent until flooding results | 3/minor | 3/minor | Low | Because most drainage systems are unlikely to be renewed over this time period movement/misalignment/distortion could become more pronounced as a result of longer wetter winters | Current asset condition and inventory not well understood. Potential to impact assets not easy to understand | Risks to subterranean and surface infrastructure from subsidence
DR2 | Asset | Drainage | Pump | Heavy rain/cloudburst | Direct | Pump failure due to work rate/failure to keep pace with rising water levels | Whole country | Professional Head of Drainage and Off Track | Linked to trigger level for investment which is asset condition/potential to compromise serviceability of track (submerged railhead/track circuit) | When pumping rates cannot keep pace with rising groundwater levels track circuit may fail/water over the rail head may prevent normal running of trains | 12/major | Medium | Although general asset inventory for drainage is only partially known/pumps are fairly well documented | 12/major | 12/major | Low | Projected increased average rainfall levels and wettest day are likely to put a strain on pumps which are already located in flood vulnerable areas. Wetter winters are likely to result in increased groundwater levels and rainfall runoff resulting in pumps potentially running for longer and being overwhelmed by higher peak flows. More intense summer convective storms are also likely to result in higher peak flows. This will impact | Confidence around specific pump assets ability to cope difficult to assess as multiple location specific factors (e.g. hydrology ) will contribute That current funding for existing management practices will remain available | Risks to infrastructure services from river, surface water and groundwater flooding
DR3 | Asset | Drainage | Pump | Heavy rain/cloudburst | Direct | Failure to acquire or difficulty acquiring statutory consent for pumps in emerging areas of flood risk | Whole country | Professional Head of Drainage and Off Track | Emergent flooding at locations not experiencing flooding before requiring pumped solutions in order to keep track serviceable | Increasing pressure on water resources (groundwater) resulting in increased regulatory pressure (e.g. new water abstraction licences depend on catchment demand) could result in limited ability to deploy pumped solutions at emergent flood locations. This could lead to the requirement for major capital works | 4/moderate | Medium | Future flood locations difficult to predict without comprehensive hydrological data | 12/major | 12/major | Low | Wetter winters are likely to result in increased groundwater levels and rainfall runoff which could contribute to the emergence of new flood risk (increased flooding at existing sites and new flood sites). Increasing pressure on water resources caused by hotter drier summers could result in a more scrutinous regulatory environment depending on how the EA/Defra choose to regulate pumped infrastructure on the railway | Assumption that the regulators continue to consent pumped abstraction in the current way in the light of hotter, drier summers. Projected increased average rainfall levels and wettest day resulting in emergent and increased flooding at new and existing locations respectively | Risks to infrastructure services from river, surface water and groundwater flooding
DR4 | Asset | Drainage | Track/earthwork drainage | Heavy rain/cloudburst | Direct | Design capacity of drainage network exceeded and system surcharges are potentially compromising parent assets | Whole country | Professional Head of Drainage and Off Track | When condition of parent asset is affected (Wetbeds, Track quality, Flooding & Earthwork stability) | Wetter winters could result in design capacity of both track and geotechnical drainage systems being exceeded compromising the integrity of parent assets. As drainage systems are likely to have been designed to local historical storm patterns this effect is likely to transpire across the whole country | 12/major | Medium | Difficult to assess as the drainage inventory is incomplete and asset design information is not available or is incomplete (as-built drawings etc). However reasonable assumption that older drainage will degrade and is unlikely to have been designed with climate change needs in mind | 12/major | 12/major | Low | Wetter winters are likely to result in increased groundwater levels and rainfall runoff resulting in increased possibility of drainage systems being overwhelmed by higher peak flows. Higher peak flows are also more likely for more intense summer convective storms | That maintenance and construction will follow current standards. That older drainage will degrade and is unlikely to have been designed with climate change needs in mind | Risks to infrastructure services from river, surface water and groundwater flooding
DR5 | Asset | Drainage | Track/earthwork drainage | Long hot, dry summer | Direct | Self cleansing water velocity not achieved for long periods causing increased siltation | Whole country | Professional Head of Drainage and Off Track | Linked to trigger level for investment which is asset condition/ drainage failing to function as designed for NR managed assets/flood events for third party lineside neighbouring assets | Hotter drier summers could lead to periods of drought. This could result in drainage systems achieving self cleansing velocity for less of the time causing greater amounts of solids to drop out. As drainage systems are likely to have been designed to local historical storm patterns this effect is likely to transpire across the whole country | 3/minor | Low | Difficult to assess as drainage inventory incomplete and asset design information not available or incomplete (As-built drawings etc) | 12/major | 12/major | Low | Hotter drier summers will increase the risk that there will be longer and more frequent periods of drought possibly resulting in self cleansing velocities in flow being achieved for less of the time | Presumption that installed drainage systems are designed to local historical rainfall patterns and don't account for climate change | Risk to transport from high and low temperatures, high winds, lightning
DR6 | Asset | Drainage | Sustainable Drainage Systems (SuDS) infrastructure | Long wet winter/spring | Direct | Storage capacity becoming insufficient to manage multiple storms in sequence combined with critical storms resulting in a higher volume balance | Whole country | Professional Head of Drainage and Off Track | Linked to trigger level for investment which is asset condition/ drainage failing to function as designed for NR managed assets/Flood events for third party lineside neighbouring assets | SuDS infrastructure will be designed to attenuate flows, primarily to reduce downstream flood risk. It is likely to have been designed with sufficient storage to accommodate a 'critical storm' (storm of a duration and intensity resulting in the largest storage requirement for a given discharge). Longer wetter winters and more intense summer storms could result in insufficient storage capacity leading to exceedance events and possible consequent flooding | 3/minor | Low | Most SuDS will have been designed with a factor of safety for climate change. Some residual risk remains because of lack of maintenance and SuDS from third party lineside development | 3/minor | 3/minor | Low | Longer wetter winters and more intense summer storms could result in insufficient storage capacity leading to exceedance events and possible consequent flooding. Increased residual risk over period of time to 2050/2080 | Presumption that Suds systems may not have been designed to accommodate projected climate change to 2050/80 | Risks to infrastructure services from river, surface water and groundwater flooding
DR7 | Asset | Drainage | Non-return valves/river outfalls | Long wet winter/spring | Direct | Wet winters increase river levels and flows in systems, resulting in flap valve levels becoming inappropriate, leading to flooding | Whole country | Professional Head of Drainage and Off Track | When condition of parent asset is affected (Wetbeds, Track quality, Flooding & Earthwork stability) | Outfalls are likely to have been set at antecedent levels for all locations across the country and therefore all locations could be affected by increases in river flows. If non return valves and outfalls are prevented from allowing outflow by higher downstream water levels, flooding could result | 12/major | Low | Asset inventory and its criticality unlikely to be fully understood. Interaction/ interdependence/phase of operation of disparate flood defence infrastructure on and off the railway is not necessarily understood, resulting in a potential increase in flood risk to railway and lineside neighbours | 16/major | 16/major | Low | Longer wetter winters are likely to increase effective flood levels in the longer term. Without increased understanding of catchment wide flood levels and modification of levels of existing outfalls and associated upstream drainage systems increased flooding may result | Very poor understanding of how catchment wide hydrology interacts with railway drainage systems and is exacerbated by increasing lineside development. More modern drainage systems and flood defence schemes are likely to have been designed with climate change isostatic rebound and consequent raised water levels in mind but older systems are vulnerable | Risks to infrastructure services from river, surface water and groundwater flooding | Risks to infrastructure services from coastal flooding and erosion
DR7a | Asset | Drainage | Non-return valves/coastal outfalls | Flooding | Direct | Rising sea levels resulting in flap valve levels becoming inappropriate, leading to flooding. (the combined effect of sea level rise and isostatic rebound are producing larger impacts in the Southern areas of England) | Whole country | Professional Head of Drainage and Off Track | When condition of parent asset is affected (Wetbeds, Track quality, Flooding & Earthwork stability) | Outfalls are likely to have been set at antecedent levels for all locations across the country and therefore all locations could be affected by increases in sea level. If non return valves and outfalls are prevented from allowing outflow flooding could result | 12/major | Low | Asset inventory and its criticality unlikely to be fully understood. Interaction/ interdependence/phase of operation of disparate flood defence infrastructure on and off the railway is not necessarily understood, resulting in a potential increase in flood risk to railway and lineside neighbours | 16/major | 16/major | Low | The effects of isostatic rebound in the south of England is likely to increase effective flood levels in the longer term. Without increased understanding of catchment wide flood levels and modification of levels of existing outfalls and associated upstream drainage systems increased flooding may result | Very poor understanding of how catchment wide hydrology interacts with railway drainage systems and is exacerbated by increasing lineside development. More modern drainage systems and flood defence schemes are likely to have been designed with climate change isostatic rebound and consequent raised water levels in mind but older systems are vulnerable | Risks to infrastructure services from coastal flooding and erosion
DR8 | Asset | Drainage | Flood defences/revetments | Long wet winter/spring | Direct | Increased river/estuarine flows resulting from longer wetter winters result in flood defences being challenged and overwhelmed with resulting flooding of the railway | Whole country | professional Head of Drainage and Off Track/ Professional Head of Structures/ Professional Head of Geotechnical | When condition of parent asset is affected (Wetbeds, Track quality, Flooding & Earthwork stability)/ Flooding of third party land through failure to maintain assets as a flood defence 'structure' | Flood defence structures challenged and overwhelmed by rising river/estuarine water levels, leading to flooding which can compromise railway performance. Structures most structures deliberately designed to protect the railway from flooding will have been built in a time when climate change was not considered and freeboard/factor of safety where structures have been designed as a flood defence may not prove to be adequate. Railway structures such as bridges, earthworks or revetments can also act as flood defences whether or not this is their primary design purpose. In some cases the assets may be designated as statutory flood defence under Schedule 1 of the Flood & Water Management Act 2010 | 12/major | Low | Current asset inventory and condition not necessarily known/ understood. Effect on flooding and flood management not necessarily understood particularly on a catchment wide basis and or multi agency management basis | 12/major | 16/major | Low | Risk is likely to increase over longer period with the trend to longer wetter winters | Asset inventory and condition likely not to be understood especially in the context of catchment wide flood management. As flood defences tend to be high profile and are likely to be monitored to an enhanced frequency based on condition, the risk is not likely to get worse over the medium term but will worsen over the longer period. Flood defence is constantly updated/reviewed to deal with rising water levels but not in relation to climate change projections. | Risks to infrastructure services from river, surface water and groundwater flooding
DR8a | Asset | Drainage | Flood defences/revetments | Heavy rain/cloudburst | Direct | Increased river/estuarine flows resulting from longer wetter winters result in flood defences being challenged and overwhelmed with resulting flooding of the railway | Whole country | professional Head of Drainage and Off Track/ Professional Head of Structures/ Professional Head of Geotechnical | When condition of parent asset is affected (Wetbeds, Track quality, Flooding & Earthwork stability)/ Flooding of third party land through failure to maintain assets as a flood defence 'structure' | Flood defence structures challenged and overwhelmed by rising river/estuarine water levels, leading to flooding which can compromise railway performance. Structures most structures deliberately designed to protect the railway from flooding will have been built in a time when climate change was not considered and freeboard/factor of safety where structures have been designed as a flood defence may not prove to be adequate. Railway structures such as bridges, earthworks or revetments can also act as flood defences whether or not this is their primary design purpose. In some cases the assets may be designated as statutory flood defence under Schedule 1 of the Flood & Water Management Act 2010 | 12/major | Low | Current asset inventory and condition not necessarily known/ understood. Effect on flooding and flood management not necessarily understood particularly on a catchment wide basis and or multi agency management basis | 12/major | 16/major | Low | Risk is likely to increase over longer period with the trend to longer wetter winters as current drainage system designs meet local historical rainfall patterns. | Asset inventory and condition likely not to be understood especially in the context of catchment wide flood management. As flood defences tend to be high profile and are likely to be monitored to an enhanced frequency based on condition, the risk is not likely to get worse over the medium term but will worsen over the longer period. Flood defence is constantly updated/reviewed to deal with rising water levels but not in relation to climate change projections. | Risks to infrastructure services from river, surface water and groundwater flooding
DR8b | Asset | Drainage | Coastal defences/revetments | Flooding | Direct | Sea level rise resulting from global sea level rise and isostatic rebound challenging flood defences with resulting flooding of the railway | Coastal | professional Head of Drainage and Off Track/ Professional Head of Structures/ Professional Head of Geotechnical | When condition of parent asset is affected (Wetbeds, Track quality, Flooding & Earthwork stability)/ Flooding of third party land through failure to maintain assets as a flood defence 'structure' | Flood defence structures may become overwhelmed by rising coastal water levels, leading to flooding which could compromise railway performance. Most structures deliberately designed to protect the railway from flooding will have been built in a time when climate change was not considered and freeboard/factor of safety may not prove to be adequate. Railway structures such as bridges, earthworks or revetments can also act as flood defences whether or not this is their primary design purpose. In some cases the assets may be designated as statutory flood defence under Schedule 1 of the Flood & Water Management Act 2010 | 12/major | Low | Current asset inventory and condition not necessarily known/ understood. Effect on flooding and flood management not necessarily understood particularly on a catchment wide basis and or multi agency management basis | 12/major | 16/major | Low | Risk is likely to increase over longer period with the trend in sea level rise. This will be exacerbated in the long term in southern England by isostatic rebound | Asset inventory and condition likely not to be understood especially in the context of catchment wide flood management. As flood defences tend to be high profile and are likely to be monitored to an enhanced frequency based on condition, the risk is not likely to get worse over the medium term but will worsen over the longer period. Flood defence is constantly updated/reviewed to deal with rising water levels but not in relation to climate change projections | Risks to infrastructure services from coastal flooding and erosion
DR9 | Asset | Drainage | Underground piped drainage | Low soil moisture | Direct | Desiccation in hotter drier summers and consequent shrinking of soils could result in misalignment of pipes and collapse of already damaged pipes and culverts with a resultant reduction in performance | Whole country | Professional Head of Drainage and Off Track | Linked to trigger level for investment which is asset condition/ drainage failing to function as designed for NR managed assets/ flood events for third party lineside neighbour assets | More extreme desiccation and wetting of soils has the potential to increase movement resulting from shrinking and swelling of soils. Open jointed or damaged pipes and culverts may be compromised in terms of their ability to manage flows | 3/minor | Low | Up to date condition data on an asset that is buried is difficult to ascertain. Damage may not be apparent until flooding results | 3/minor | 3/minor | Low | Because most drainage systems are unlikely to be renewed over this time period movement/misalignment/distortion could become more pronounced as a result of hotter drier summers | Current asset condition and inventory not well understood. Potential to impact assets not easy to understand | Risks to subterranean and surface infrastructure from subsidence
Geo1 | Asset | Geotechnical | Rock cuttings, soil cuttings, embankments | Long hot, dry summer | Direct | Clay shrinkage of embankments will result in deterioration of track geometry and subsequently performance impacts | Whole country | Professional Head of Geotechnical | Earthwork Evaluation is the business process during which threats and consequences are considered holistically and management strategies including interventions and mitigations determined | Increased extremes of wetting and drying increase the rate of deterioration, demonstrated through academic research programmes. More extreme cyclical processes between the summer and winter will require greater levels of investment to maintain the levels of performance in predominantly clay areas (mostly the south-east) | 12/major | High | Potentially high consequence events in 2019/20 with potential for 2-10 fatalities, c.£200m/yr geotechnical spend, 10 lines closed simultaneously at one point in February due to earthworks failures | 25/severe | 25/severe | Medium | Spending will almost certainly need to exceed £250m/yr by 2050 to control risks associated with earthworks if all else remains consistent until then | Assumes current levels of intervention/mitigation activity, which in the long run are unsustainably low without factoring in climate change adaptation | Risks to transport networks from slope and embankment failure | Risk to transport from high and low temperatures, high winds, lightning
Geo2 | Asset | Geotechnical | Rock cuttings, soil cuttings, embankments | Heavy rain/ cloudburst | Direct | Long-term degradation, adverse/extreme weather, surface water, scour and groundwater lead to asset failure with little or no precursor to the failure. These events can cause serious safety concerns and significant performance impacts | Whole country | Professional Head of Geotechnical | Earthwork Evaluation is the business process during which threats and consequences are considered holistically and management strategies including interventions and mitigations determined | Such events highlight the underlying lack of resistance in the earthwork portfolio. There is a balance needed to adequately invest in strengthening to make infrastructure more resistant and mitigating short-term increases in safety risk as short notice storms occur, then responding & recovering quickly should an asset failure occur | 12/major | High | Potentially high consequence events in 2019/20 with potential for 2-10 fatalities, c.£200m/yr geotechnical spend, 10 lines closed simultaneously at one point in February due to earthworks | 25/severe | 25/severe | Medium | Spending will almost certainly need to exceed £250m/yr by 2050 to control risks associated with earthworks if all else remains consistent until then | Assumes current levels of intervention/mitigation activity, which in the long run are unsustainably low without factoring in climate change adaptation | Risks to transport networks from slope and embankment failure | Risks to infrastructure services from river, surface water and groundwater flooding Risks to infrastructure services from coastal flooding and erosion Risks to subterranean and surface infrastructure from subsidence
Geo3 | Asset | Geotechnical | Rock cuttings, soil cuttings, embankments | High average rainfall over several days | Direct | Prolonged periods of wet weather increase the likelihood of asset failure as the ground becomes saturated. Every asset will have a limit of resistance to saturation as most are >150 years old | Whole country | Professional Head of Geotechnical | Earthwork Evaluation is the business process during which threats and consequences are considered holistically and management strategies including interventions and mitigations determined | Increased extremes of wetting and drying increase the rate of deterioration, demonstrated through academic research programmes. A prolonged wet period (e.g. winter 2013/14) will cause problems that become immediately apparent and interrupt operations, but also create longer term problems with a large proportion of assets that have been extensively stressed but not quite to the point of failure | 12/major | High | Potentially high consequence events in 2019/20 with potential for 2-10 fatalities, c.£200m/yr geotechnical spend, 10 lines closed simultaneously at one point in February due to earthworks | 25/severe | 25/severe | Medium | Spending will almost certainly need to exceed £250m/yr by 2050 to control risks associated with earthworks if all else remains consistent until then | Assumes current levels of intervention/mitigation activity, which in the long run are unsustainably low without factoring in climate change adaptation | Risks to transport networks from slope and embankment failure | Risks to infrastructure services from river, surface water and groundwater flooding Risks to infrastructure services from coastal flooding and erosion Risks to subterranean and surface infrastructure from subsidence
Geo4 | Asset | Geotechnical | Rock cuttings, soil cuttings, embankments | Long hot, dry summer | Direct | Repeated periods of hot dry weather lead to drying of soils and shrinkage as part of cyclical processes such as seasonal shrink/swell in tandem with seasonal wetting. This can cause degradation and failures with other age driven processes | Whole Country | Professional Head of Geotechnical | Earthwork Evaluation is the business process during which threats and consequences are considered holistically and management strategies including interventions and mitigations determined | Increased extremes of wetting and drying increase the rate of deterioration, demonstrated through academic research programmes. | 12/major | High | Potentially high consequence events in 2019/20 with potential for 2-10 fatalities, c.£200m/yr geotechnical spend, 10 lines closed simultaneously at one point in February due to earthworks | 25/severe | 25/severe | Medium | Spending will almost certainly need to exceed £250m/yr by 2050 to control risks associated with earthworks if all else remains consistent until then | Assumes current levels of intervention/mitigation activity, which in the long run are unsustainably low without factoring in climate change adaptation | Risks to transport networks from slope and embankment failure | Risks to subterranean and surface infrastructure from subsidence Risk to transport from high and low temperatures, high winds, lightning
Geo5 | Asset | Geotechnical | Rock cuttings, soil cuttings, embankments | Snow/ice | Direct | Long term degradation due to age-driven/cyclical processes such as freeze thaw and snowmelt | Whole Country | Professional Head of Geotechnical | Earthwork Evaluation is the business process during which threats and consequences are considered holistically and management strategies including interventions and mitigations determined | Historical and ongoing extreme cold weather events and the associated thawing have long-term degradation effects on geotechnical assets | 12/major | High | Potentially high consequence events in 2019/20 with potential for 2-10 fatalities, c.£200m/yr geotechnical spend, 10 lines closed simultaneously at one point in February due to earthworks | 25/severe | 25/severe | Medium | As cold weather events are projected to reduce in frequency this pressure could ease, however the continued aging of assets may offset this and spending will almost certainly need to exceed £250m/yr by 2050 to control risks associated with earthworks if all else remains consistent until then | Assumes current levels of intervention/mitigation activity, which in the long run are unsustainably low without factoring in climate change adaptation | Risks to transport networks from slope and embankment failure | Risks to subterranean and surface infrastructure from subsidence Risk to transport from high and low temperatures, high winds, lightning
LX1 | Asset | Level crossing | Level crossing | High winds | Direct | Failure of barriers | Whole country | Professional Head of Level Crossing | At point of failure or advance weather warning | There is a risk across the country although the risk will be higher in the exposed areas where the wind speed will be higher | 9/Moderate | Medium | Historic evidence from Level Crossing barrier failures provides sufficient knowledge of potential failure risks | 9/moderate | 12/major | Medium | Not expecting any significant increase in wind speeds; Ref Section 11. Likely to be an increase in storms and gusts | Assumptions based on current asset location and knowledge of surrounding environmental conditions | Risk to transport from high and low temperatures, high winds, lightning
LX2 | Asset | Level crossing | Level crossing | Storms | Direct | Failure of barriers | Whole country | Professional Head of Level Crossing | At point of failure or advance weather warning | There is a risk across the country although the risk will be higher in the exposed areas where the wind speed will be higher | 9/Moderate | Medium | Historic evidence from Level Crossing barrier failures provides sufficient knowledge of potential failure risks | 9/moderate | 12/major | Medium | Not expecting any significant increase in wind speeds; Ref Section 11. Likely to be an increase in storms and gusts | Assumptions based on current asset location and knowledge of surrounding environmental conditions. | Risks to infrastructure services from river, surface water and groundwater flooding | Risk to transport from high and low temperatures, high winds, lightning
LX3 | Asset | Level crossing | Level crossing | Flooding | Direct | Flooding of loc case and/or barrier machine | Whole country | Professional Head of Level Crossing | At point of failure or advance weather warning | There is a risk across the country although the risk will be higher in areas prone to flooding | 6/moderate | Medium | Historic evidence from Level Crossing barrier machine and location case failures provides sufficient knowledge of potential failure risks | 6/moderate | 12/major | Medium | Significant increase in rainfall leading to flooding; Ref Section 7. This increasing change will increase future flood risk | Precipitation predictions from UKCP09 | Risks to infrastructure services from river, surface water and groundwater flooding
LX4 | Asset | Level crossing | Level crossing | Snow/ice | Direct | Road traffic lights and warning lights obscured, visibility of CCTV obscured, operation of boom affected, obstacle detection affected | Whole country | Professional Head of Level Crossing | At point of failure or advance weather warning | Greater risk for Northern areas | 4/moderate | Medium | Dense snowfall could affect visibility of RTLs but this is not currently an issue. Circular cross section of boom means snow is unable to build up on the boom. Historically snow has effected OD equipment but mitigations are effective | 4/moderate | 4/moderate | Medium | The climate change projections state that modelling future snow is challenging. However, it generally states there will be a reduction in snow fall. As there is limited confidence in the modelling of snow fall the projected risk has been left as the current risk | Assumptions based on current asset location and knowledge of surrounding environmental conditions | Risk to transport from high and low temperatures, high winds, lightning
LX5 | Asset | Level crossing | Level crossing | Extreme hot days | Direct | Control and peripheral equipment overheats | Whole country | Professional Head of Level Crossing | At point of failure or advance weather warning | Equipment located in passive loc cases at risk of overheating, particularly where sun hats are not used and orientation gives the worst solar gain | 4/moderate | Medium | Historic information shows that there is a small increase in failures on hot days but it is not significant | 6/moderate | 9/moderate | Medium | There is currently no strong correlation between high temperatures and level crossing failures. It is therefore difficult to interpolate how increasing temperatures will affect level crossings. It can be assumed to that increased temperatures will affect control equipment and PSUs but the extent is unknown | This analysis assumes that treadles are considered as a separate asset | Risk to transport from high and low temperatures, high winds, lightning
OLE 1 | Asset | OLE | Wire run auto tension (single stack balance weights) | Extreme hot days | Direct | Weights reach full downward movement | Whole country | Professional Head of Contact Systems | Ambient temperatures reaches over 38 deg C (design range limits) | Records show we have not had issues through high temperatures previously, only in isolated locations going back to hot spells in 1976 | 4/moderate | Medium | If the wire run is maintenance free, with no heat related defects with sufficient play on the balance weights the risk is low to medium | 8/moderate | 12/major | Medium | Future design changes will be required to the OLE to allow for the predicted high temperatures | Latest OLE designs have used spring tensioners, which have the capacity to work up to a higher temperature range. Current systems are to be maintained and adjusted to meet the higher temperature ranges, including work on the wire interface areas (crossovers/overlaps) | Risk to transport from high and low temperatures, high winds, lightning
OLE 2 | Asset | OLE | Wire run auto tension (single stack balance weights) stretch recovery repairs not completed | Heat wave | Direct | Weights reach full downward movement | Whole country | Professional Head of Contact Systems | Ambient temperatures reaches over 25 deg C (Design range limits) | Records show we have a number of wire runs that have not had stretch recovery work completed | 6/moderate | High | The mitigations are through carrying out patrols to identify the risk and carry out mitigation work to allow for more downward movement on the stack of weights | 8/moderate | 12/major | Medium | Future design changes will be required to the OLE to allow for the predicted high temperatures | Latest OLE designs have used spring tensioners, which have the capacity to work up to a higher temperature range, or to adjust the anchor to a single wheel twin stack arrangement: key factors to address * Longer track access, to adjust and maintain * Improve the skills fade | Risk to transport from high and low temperatures, high winds, lightning
OLE 3 | Asset | OLE | Wire run fixed termination | Extreme hot days | Direct | Loss of tension in the wire, leading to pantograph hook over | Whole country | Professional Head of Contact Systems | Ambient temperatures reach over 38 deg C (Design range limits) | Previous records through the 1976 heatwave no issues were recorded, 2019 was the first time this has been recorded, due to low tensioned wire runs | 12/major | High | When temperatures reach above 38 deg C, creates sag in the wire. Greater risk at sites where there are converging and diverging wires. Risk also increased where projects have been working in the area and making basic adjustments that will interfere with the tensions. Track access at such sites is also limited and this is essential to carry out the work. (below specification) Understand and manage areas where we have low wire heights | 8/moderate | 12/major | High | Changing the wire to auto tensioned equipment is one future option, but this will also raise other issues with along track movement wear and tear. We could look at increasing the tensions and strengthen the areas where we have converging and diverging wires | Current plans are to check tensions on fixed terminations and make adjustments when required: Key factors to address * Longer track access, to adjust and maintain * Improve the skills fade into knowledge of fixed terminations equipment This type of equipment is not mainline affecting but exists in mainline terminal stations | Risk to transport from high and low temperatures, high winds, lightning
OLE 4 | Asset | OLE | Wire run auto tension (spring tension device) | Extreme hot days | Direct | Loss of tension in the wire | Whole country | Professional Head of Contact Systems | Ambient temperatures reach over 40 deg C (Design range limits) | No historic records for this type of failure on this device at these temperatures | 3/minor | Medium | When temperatures reach above 40 deg C, there is enough tolerance to take it slightly higher. Work with the manufacturer to understand the risk at higher temperatures then specified | 9/moderate | 12/major | Low | Interim measures can be made to make adjustments and setting changes to spring tensioners; but this will be limited because the range of adjustment will limit the length of the wire run | The current plans is to monitor the tensioners in extreme temperature conditions & work with Pfisterer to understand the full risk | Risk to transport from high and low temperatures, high winds, lightning
OLE 5 | Asset | OLE | Neutral section | Extreme hot days | Direct | Poor performance to risk of dewirement | Whole country | Professional Head of Contact Systems | Ambient temperatures reach over 38/40 deg C (design range limits) | No historic records for this type of failure on this device, but blank speeds will reduce the risk | 3/minor | Medium | Through high temperatures the risk is when the weights have reached its lower limits or extent of travel on the tensorex, causing loss of tension | 8/moderate | 12/major | Medium | Future design changes will be required to the OLE to allow for the predicted high temperatures | The current plans is to monitor the balance weights in extreme temperature conditions, and apply blanket speed to limit the risk. Also making sure the profile set-up is in order | Risk to transport from high and low temperatures, high winds, lightning
OLE 6 | Asset | OLE | Section insulators | Extreme hot days | Direct | Poor performance to risk of dewirement for both auto tension and fixed termination wire runs | Whole country | Professional Head of Contact Systems | Ambient temperatures reach over 38 / 40deg C (Design range limits) | No historic records for this type of device, but blank speeds will reduce the risk | 3/minor | Medium | Through high temperatures the risk is when the weights have bottomed out, causing failure | 8/moderate | 12/major | Medium | Future design changes will be required to the OLE to allow for the predicted high temperatures | The current plans is to monitor the balance weights in extreme temperature conditions, and apply blanket speed to limit the risk. Also making sure the profile set-up is in order | Risk to transport from high and low temperatures, high winds, lightning
PD02 | Asset | Power Distribution | HV power system protection | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 6/moderate | High | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD03 | Asset | Power Distribution | Changeover Panels | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 4/moderate | High | More likely than a direct strike, but far easier to repair | 4/moderate | 6/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD04 | Asset | Power Distribution | Distribution network operator supplies | Flooding | Interdependency (us on them) | Flooding can affect power supplies | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 9/moderate | Medium | Current typical flood levels are known and accounted for | 9/moderate | 12/major | Low | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist
PD05 | Asset | Power Distribution | Distribution network operator supplies | Lightning | Interdependency (us on them) | Impulse from a lightning strike elsewhere on the network can interrupt electrical supply | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | Medium | Unlikely but can have devastating effects | 9/moderate | 12/major | Low | Lightning strikes across the country will increase | Assuming general increase in storm frequency and severity | Risks to energy from high and low temperatures, high wind, lightning | Risk to transport from high and low temperatures, high winds, lightning
PD06 | Asset | Power Distribution | Distribution network operator supplies | Storms | Interdependency (us on them) | Distribution Network Operator supplies are more likely to fluctuate during inclement weather | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | Medium | Unlikely. Mitigations generally effective, where applied | 9/moderate | 12/major | Low | Storm frequency and severity is likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to energy from high and low temperatures, high wind, lightning | Risks to infrastructure services from river, surface water and groundwater flooding
PD07 | Asset | Power Distribution | Functional supply points | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD08 | Asset | Power Distribution | Functional supply points | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Asset is generally capable of withstanding current range of temperatures | 4/moderate | 6/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD09 | Asset | Power Distribution | Functional supply points | Low soil moisture | Direct | Low soil moisture content can increase earthing resistance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 3/minor | Low | This issue often goes undetected | 3/minor | 6/moderate | Low | Effects of low soil moisture will manifest more often and for longer periods | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD1 | Asset | Power Distribution | AC power supply conditioning | Extreme hot days | Direct | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 6/moderate | 8/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD10 | Asset | Power Distribution | Functional supply points | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Low | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD100 | Asset | Power distribution | Lighting support structure | High winds | Direct | Excess wind loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is exposed | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | High wind speeds are likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD101 | Asset | Power distribution | Lighting support structure | Storms | Direct | Storms can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Storm frequency and severity is likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding | Risk to transport from high and low temperatures, high winds, lightning
PD102 | Asset | Power distribution | Signal box: power supply >120V | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 6/moderate | 6/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD103 | Asset | Power distribution | Signal box: power supply >120V | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 6/moderate | 9/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD104 | Asset | Power distribution | Signal box: power supply >120V | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD105 | Asset | Power distribution | Signal box: power supply >120V | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 6/moderate | Medium | Current typical flood levels are known and accounted for | 6/moderate | 9/moderate | Low | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD106 | Asset | Power distribution | Signal box: power supply >120V | Erosion | Direct | Erosion can expose structure foundations and buried cables, and increase earthing resistances | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 6/moderate | Medium | Current asset condition known, mitigations generally effective | 6/moderate | 9/moderate | Low | Controls are effective, but damage to these assets will be service-affecting until repaired or replaced | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD107 | Asset | Power distribution | Signal box: power supply >120V | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 6/moderate | Low | Unlikely but can have devastating effects | 6/moderate | 6/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD108 | Asset | Power distribution | Signal box: power supply >120V | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | Medium | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Low | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD109 | Asset | Power distribution | 1500V DC/1500V HV cables | Extreme hot days | Direct | High temperatures degrade cable performance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 4/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD11 | Asset | Power Distribution | Functional supply points | Erosion | Direct | Erosion can expose surface and buried cables and increase earthing resistances | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 4/moderate | Medium | Current asset condition known, mitigations generally effective | 4/moderate | 6/moderate | Low | Asset is typically sited trackside and exposed to the elements | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD110 | Asset | Power distribution | AC power supply conditioning | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD111 | Asset | Power distribution | Battery & charger | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD112 | Asset | Power distribution | 1500V DC cables | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD113 | Asset | Power distribution | 1500V DC cables | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 4/moderate | Low | Unlikely but can have devastating effects | 4/moderate | 4/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD114 | Asset | Power distribution | 1500V DC cables | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 4/moderate | Medium | More likely than a direct strike, but far easier to repair | 4/moderate | 6/moderate | Low | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD115 | Asset | Power distribution | 1500V DC/1500V HV switchgear | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 4/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD116 | Asset | Power distribution | 1500V DC/1500V HV switchgear | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 6/moderate | 9/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD117 | Asset | Power distribution | 1500V DC switchgear | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulating media | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 3/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 3/minor | 6/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD118 | Asset | Power distribution | 1500V DC/1500V HV switchgear | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD119 | Asset | Power distribution | Insulation monitoring devices | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 4/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD12 | Asset | Power Distribution | Auxiliary transformer | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 4/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD120 | Asset | Power distribution | 1500V DC switchgear | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 4/moderate | Low | Unlikely but can have devastating effects | 4/moderate | 4/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD121 | Asset | Power distribution | 1500V DC switchgear | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 4/moderate | Medium | More likely than a direct strike, but far easier to repair | 4/moderate | 6/moderate | Low | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD122 | Asset | Power distribution | 1500V HV cables | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD123 | Asset | Power distribution | 1500V HV cables | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 4/moderate | Low | Unlikely but can have devastating effects | 4/moderate | 4/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD124 | Asset | Power distribution | 1500V HV cables | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 4/moderate | Medium | More likely than a direct strike, but far easier to repair | 4/moderate | 6/moderate | Low | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD125 | Asset | Power distribution | Insulation monitoring devices | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD126 | Asset | Power distribution | 1500V HV switchgear | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulating media | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 3/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 3/minor | 6/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD127 | Asset | Power distribution | 1500V HV switchgear | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 8/moderate | Low | Unlikely but can have devastating effects | 8/moderate | 8/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD128 | Asset | Power distribution | 1500V HV switchgear | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | Medium | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Low | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD129 | Asset | Power distribution | 1500V HV transformer/ rectifier | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 6/moderate | 6/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD13 | Asset | Power Distribution | Functional supply points | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 6/moderate | Low | Unlikely but can have devastating effects | 6/moderate | 6/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD130 | Asset | Power distribution | 1500V HV transformer/ rectifier | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 6/moderate | 9/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD131 | Asset | Power distribution | 1500V HV transformer/ rectifier | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD132 | Asset | Power distribution | 1500V HV transformer/ rectifier | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD133 | Asset | Power distribution | 1500V HV transformer/ rectifier | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 8/moderate | Low | Unlikely but can have devastating effects | 8/moderate | 8/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD134 | Asset | Power distribution | Insulation monitoring devices | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD135 | Asset | Power distribution | 1500V HV transformer/ rectifier | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | Medium | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Low | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD136 | Asset | Power distribution | Metering | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 2/minor | 3/minor | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD137 | Asset | Power distribution | Metering | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 2/minor | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD138 | Asset | Power distribution | Metering | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | High | Current typical flood levels are known and accounted for | 2/minor | 3/minor | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD139 | Asset | Power distribution | Metering | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD14 | Asset | Power Distribution | Functional supply points | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | High | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD140 | Asset | Power distribution | Metering | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD141 | Asset | Power distribution | Points heater monitor | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 2/minor | 2/minor | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD142 | Asset | Power distribution | Points heater monitor | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 2/minor | 3/minor | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD143 | Asset | Power distribution | Points heater monitor | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 2/minor | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD144 | Asset | Power distribution | Insulation monitoring devices | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD145 | Asset | Power distribution | Points heater monitor | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | High | Current typical flood levels are known and accounted for | 2/minor | 3/minor | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD146 | Asset | Power distribution | Points heater monitor | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD147 | Asset | Power distribution | Points heater monitor | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD148 | Asset | Power distribution | Power supply monitor | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 2/minor | 2/minor | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD149 | Asset | Power distribution | Power supply monitor (including signal power) | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 2/minor | 3/minor | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD15 | Asset | Power Distribution | Functional supply points | High winds | Direct | Excess wind loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is exposed | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 6/moderate | Low | High wind speeds are likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD150 | Asset | Power distribution | Power supply monitor | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 2/minor | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD151 | Asset | Power distribution | Power supply monitor (including signal power) | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | High | Current typical flood levels are known and accounted for | 2/minor | 3/minor | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD152 | Asset | Power distribution | Power supply monitor | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD153 | Asset | Power distribution | Power supply monitor | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD154 | Asset | Power distribution | Signal power supply monitor | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 2/minor | 2/minor | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD155 | Asset | Power distribution | Insulation monitoring devices | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD156 | Asset | Power distribution | Signal power supply monitor | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 2/minor | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD157 | Asset | Power distribution | Signal power supply monitor | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD158 | Asset | Power distribution | Signal power supply monitor | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD159 | Asset | Power distribution | UPS management | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 2/minor | 2/minor | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD16 | Asset | Power distribution | Functional supply points | Storms | Direct | Storms can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 6/moderate | Low | Storm frequency and severity is likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning | Risks to infrastructure services from river, surface water and groundwater flooding
PD160 | Asset | Power distribution | UPS management | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 2/minor | 3/minor | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD161 | Asset | Power distribution | UPS management | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 2/minor | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD162 | Asset | Power distribution | UPS management | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | High | Current typical flood levels are known and accounted for | 2/minor | 3/minor | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD163 | Asset | Power distribution | UPS management | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD164 | Asset | Power distribution | Insulation monitoring devices | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD165 | Asset | Power distribution | UPS management | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD166 | Asset | Power distribution | TPCMS equipment (all) | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 4/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD167 | Asset | Power distribution | TPCMS equipment (all) | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD168 | Asset | Power distribution | TPCMS equipment (all) | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 2/minor | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD169 | Asset | Power distribution | TPCMS equipment (all) | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD17 | Asset | Power distribution | LV autorecloser | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 4/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD170 | Asset | Power distribution | TPCMS equipment (all) | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 4/moderate | Low | Unlikely but can have devastating effects | 4/moderate | 4/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD171 | Asset | Power distribution | TPCMS equipment (all) | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 4/moderate | High | More likely than a direct strike, but far easier to repair | 4/moderate | 6/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD172 | Asset | Power distribution | Points heating | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of rails to which this equipment is attached | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Low | Asset is generally capable of withstanding current range of temperatures | 2/minor | 3/minor | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD173 | Asset | Power distribution | Points heating | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | High | Current typical flood levels are known and accounted for | 2/minor | 3/minor | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD174 | Asset | Power distribution | Points heating | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD175 | Asset | Power distribution | Integrated protection and control | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 4/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD176 | Asset | Power distribution | Points heating | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD177 | Asset | Power distribution | Asset walkway lighting | Ice/Hail | Direct | Excess snow and ice loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 1/minor | Low | Incidence of ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD178 | Asset | Power distribution | Asset walkway lighting | Snow/ice | Direct | Snow and ice can affect structure loading | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 1/minor | Low | Incidence of snow/ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD179 | Asset | Power distribution | Asset walkway lighting | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 1/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 1/minor | 2/minor | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD18 | Asset | Power distribution | LV autorecloser | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD180 | Asset | Power distribution | Asset walkway lighting | Long hot, dry summer | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 4/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD181 | Asset | Power distribution | Asset walkway lighting | Long wet winter/spring | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD182 | Asset | Power distribution | Asset walkway lighting | Heavy rain/cloudburst | Direct | Excess water can damage structures, luminaires and cables | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Increasing intense rainfall increases the risk of damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD183 | Asset | Power distribution | Asset walkway lighting | High soil moisture | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current conditions | 2/minor | 3/minor | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD184 | Asset | Power distribution | Asset walkway lighting | Low soil moisture | Direct | Low soil moisture content can affect structures and increase earthing resistance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD185 | Asset | Power distribution | Asset walkway lighting | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | High | Current typical flood levels are known and accounted for | 2/minor | 3/minor | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD186 | Asset | Power distribution | Integrated protection and control | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD187 | Asset | Power distribution | Asset walkway lighting | Erosion | Direct | Erosion can expose structure foundations and buried cables, and increase earthing resistances | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 2/minor | Medium | Current asset condition known, mitigations generally effective | 2/minor | 3/minor | Low | Increasing erosion increases risk of foundation issues | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD188 | Asset | Power distribution | Asset walkway lighting | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD189 | Asset | Power distribution | Asset walkway lighting | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD19 | Asset | Power distribution | LV autorecloser | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators. | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Asset is generally capable of withstanding current range of temperatures | 4/moderate | 6/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD190 | Asset | Power distribution | Asset walkway lighting | High winds | Direct | Excess wind loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is exposed | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | High wind speeds are likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD191 | Asset | Power distribution | Asset walkway lighting | Storms | Direct | Storms can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Storm frequency and severity is likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding | Risk to transport from high and low temperatures, high winds, lightning
PD192 | Asset | Power distribution | CCTV crossing lighting | Ice/Hail | Direct | Excess snow and ice loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 2/minor | Low | Incidence of ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD193 | Asset | Power distribution | CCTV crossing lighting | Snow/ice | Direct | Snow and ice can affect structure loading | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 2/minor | Low | Incidence of snow/ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD194 | Asset | Power distribution | CCTV crossing lighting | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Asset is generally capable of withstanding current range of temperatures | 4/moderate | 6/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD195 | Asset | Power distribution | CCTV crossing lighting | Long hot, dry summer | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 6/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action. | Risk to transport from high and low temperatures, high winds, lightning
PD196 | Asset | Power distribution | CCTV crossing lighting | Long wet winter/spring | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 6/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD197 | Asset | Power distribution | CCTV crossing lighting | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD198 | Asset | Power distribution | CCTV crossing lighting | Heavy rain/cloudburst | Direct | Excess water can damage structures, luminaires and cables | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 6/moderate | Low | Increasing intense rainfall increases the risk of damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD199 | Asset | Power distribution | CCTV crossing lighting | High soil moisture | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Structures are designed to withstand current conditions | 4/moderate | 6/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD20 | Asset | Power distribution | LV autorecloser | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Low | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD200 | Asset | Power distribution | CCTV crossing lighting | Low soil moisture | Direct | Low soil moisture content can affect structures and increase earthing resistance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 6/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD201 | Asset | Power distribution | CCTV crossing lighting | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD202 | Asset | Power distribution | CCTV crossing lighting | Erosion | Direct | Erosion can expose structure foundations and buried cables, and increase earthing resistances | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 4/moderate | Medium | Current asset condition known, mitigations generally effective | 4/moderate | 6/moderate | Low | Increasing erosion increases risk of foundation issues | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD203 | Asset | Power distribution | CCTV crossing lighting | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 4/moderate | Low | Unlikely but can have devastating effects | 4/moderate | 4/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD204 | Asset | Power distribution | CCTV crossing lighting | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 4/moderate | High | More likely than a direct strike, but far easier to repair | 4/moderate | 6/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD205 | Asset | Power distribution | CCTV crossing lighting | High winds | Direct | Excess wind loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is exposed | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 6/moderate | Low | High wind speeds are likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD206 | Asset | Power distribution | CCTV crossing lighting | Storms | Direct | Storms can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 6/moderate | Low | Storm frequency and severity is likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning | Risks to infrastructure services from river, surface water and groundwater flooding
PD207 | Asset | Power distribution | Crossing, escape, junction & siding lighting | Ice/Hail | Direct | Excess snow and ice loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 1/minor | Low | Incidence of ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD208 | Asset | Power distribution | AC power supply conditioning | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD209 | Asset | Power distribution | Integrated protection and control | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD21 | Asset | Power distribution | LV autorecloser | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 6/moderate | Low | Unlikely but can have devastating effects | 6/moderate | 6/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity. | Risk to transport from high and low temperatures, high winds, lightning
PD210 | Asset | Power distribution | Crossing, escape, junction & siding lighting | Snow/ice | Direct | Snow and ice can affect structure loading | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 1/minor | Low | Incidence of snow/ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD211 | Asset | Power distribution | Crossing, escape, junction & siding lighting | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 1/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 1/minor | 2/minor | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD212 | Asset | Power distribution | Crossing, escape, junction & siding lighting | Long hot, dry summer | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 4/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD213 | Asset | Power distribution | Crossing, escape, junction & siding lighting | Long wet winter/spring | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD214 | Asset | Power distribution | Crossing, escape, junction & siding lighting | Heavy rain/cloudburst | Direct | Excess water can damage structures, luminaires and cables | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Increasing intense rainfall increases the risk of damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD215 | Asset | Power distribution | Crossing, escape, junction & siding lighting | High soil moisture | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current conditions | 2/minor | 3/minor | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD216 | Asset | Power distribution | Crossing, escape, junction & siding lighting | Low soil moisture | Direct | Low soil moisture content can affect structures and increase earthing resistance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD217 | Asset | Power distribution | Crossing, escape, junction & siding lighting | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | High | Current typical flood levels are known and accounted for | 2/minor | 3/minor | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD218 | Asset | Power distribution | Crossing; electrification and Junction lighting/ floodlights and signage | Erosion | Direct | Erosion can expose structure foundations and buried cables, and increase earthing resistances | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition. | This is a risk across the country, particularly in areas where the asset is on earthworks | 2/minor | Medium | Current asset condition known, mitigations generally effective | 2/minor | 3/minor | Low | Increasing erosion increases risk of foundation issues | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD219 | Asset | Power distribution | Crossing lighting | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition. | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD22 | Asset | Power distribution | LV autorecloser | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | High | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD220 | Asset | Power distribution | Integrated protection and control | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition. | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 8/moderate | Low | Unlikely but can have devastating effects | 8/moderate | 8/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD221 | Asset | Power distribution | Crossing lighting | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition. | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD222 | Asset | Power distribution | Crossing, escape, junction & siding lighting | High winds | Direct | Excess wind loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition. | This is a risk across the country, particularly in areas where the asset is exposed | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | High wind speeds are likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD223 | Asset | Power distribution | Crossing, escape, junction & siding lighting | Storms | Direct | Storms can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition. | This is a risk across the country, particularly in areas where the asset is on earthworks | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Storm frequency and severity is likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding | Risk to transport from high and low temperatures, high winds, lightning
PD224 | Asset | Power distribution | Electrification signage lighting | Ice/Hail | Direct | Excess snow and ice loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition. | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 1/minor | Low | Incidence of ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD225 | Asset | Power distribution | Electrification signage lighting | Snow/ice | Direct | Snow and ice can affect structure loading | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 1/minor | Low | Incidence of snow/ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD226 | Asset | Power distribution | Electrification signage lighting | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 1/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 1/minor | 2/minor | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD227 | Asset | Power distribution | Electrification signage lighting | Long hot, dry summer | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 4/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD228 | Asset | Power distribution | Electrification signage lighting | Long wet winter/spring | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD229 | Asset | Power distribution | Electrification signage lighting | Heavy rain/cloudburst | Direct | Excess water can damage structures, luminaires and cables | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Increasing intense rainfall increases the risk of damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD23 | Asset | Power Distribution | Auxiliary transformer | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD230 | Asset | Power distribution | Electrification signage lighting | High soil moisture | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current conditions | 2/minor | 3/minor | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD231 | Asset | Power distribution | Integrated protection and control | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | High | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD232 | Asset | Power distribution | Electrification signage lighting | Low soil moisture | Direct | Low soil moisture content can affect structures and increase earthing resistance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD233 | Asset | Power distribution | Electrification signage lighting | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | High | Current typical flood levels are known and accounted for | 2/minor | 3/minor | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD234 | Asset | Power distribution | Electrification signage lighting | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD235 | Asset | Power distribution | Electrification signage lighting | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD236 | Asset | Power distribution | Electrification signage lighting | High winds | Direct | Excess wind loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is exposed | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Medium | High wind speeds are likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD237 | Asset | Power distribution | Electrification signage lighting | Storms | Direct | Storms can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Storm frequency and severity is likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from coastal flooding and erosion | Risk to transport from high and low temperatures, high winds, lightning
PD238 | Asset | Power distribution | LVAC changeover panel | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD239 | Asset | Power distribution | Escape lighting | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD24 | Asset | Power distribution | LV cables/ switchgear | Extreme hot days | Direct | High temperatures degrade cable performance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD240 | Asset | Power distribution | Escape lighting | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD241 | Asset | Power distribution | LVAC changeover panel | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD242 | Asset | Power distribution | LVAC changeover panel | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD243 | Asset | Power distribution | Junction lighting | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD244 | Asset | Power distribution | Junction lighting | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD245 | Asset | Power distribution | Navigation lighting | Ice/Hail | Direct | Excess snow and ice loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 2/minor | Low | Incidence of ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD246 | Asset | Power distribution | Navigation lighting | Snow/ice | Direct | Snow and ice can affect structure loading | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 2/minor | Low | Incidence of snow/ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD247 | Asset | Power distribution | Navigation lighting | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 1/minor | 2/minor | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD248 | Asset | Power distribution | Navigation lighting | Long hot, dry summer | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 4/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD249 | Asset | Power distribution | Navigation lighting | Long wet winter/spring | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 6/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD25 | Asset | Power distribution | LV cables | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD250 | Asset | Power distribution | LVAC changeover panel | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | High | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD251 | Asset | Power distribution | Navigation lighting | Heavy rain/cloudburst | Direct | Excess water can damage structures, luminaires and cables | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 6/moderate | Low | Increasing intense rainfall increases the risk of damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD252 | Asset | Power distribution | Navigation lighting | High soil moisture | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Structures are designed to withstand current conditions | 4/moderate | 6/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD253 | Asset | Power distribution | Navigation lighting | Low soil moisture | Direct | Low soil moisture content can affect structures and increase earthing resistance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 6/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD254 | Asset | Power distribution | Navigation lighting | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Low | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD255 | Asset | Power distribution | Navigation lighting | Erosion | Direct | Erosion can expose structure foundations and buried cables, and increase earthing resistances | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 4/moderate | Medium | Current asset condition known, mitigations generally effective | 4/moderate | 6/moderate | Low | Increasing erosion increases risk of foundation issues | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD256 | Asset | Power distribution | Navigation lighting | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 4/moderate | Low | Unlikely but can have devastating effects | 4/moderate | 4/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD257 | Asset | Power distribution | Navigation lighting | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 4/moderate | High | More likely than a direct strike, but far easier to repair | 4/moderate | 6/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD258 | Asset | Power distribution | Navigation lighting | High winds | Direct | Excess wind loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is exposed | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 6/moderate | Low | High wind speeds are likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD259 | Asset | Power distribution | Navigation lighting | Storms | Direct | Storms can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 6/moderate | Low | Storm frequency and severity is likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding | Risk to transport from high and low temperatures, high winds, lightning
PD26 | Asset | Power distribution | LV cables | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD260 | Asset | Power distribution | Route floodlighting | Ice/Hail | Direct | Excess snow and ice loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 1/minor | Low | Incidence of ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD261 | Asset | Power distribution | HV cable route | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD262 | Asset | Power distribution | Route floodlighting | Snow/ice | Direct | Snow and ice can affect structure loading | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 1/minor | Low | Incidence of snow/ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD263 | Asset | Power distribution | Route floodlighting | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 1/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 1/minor | 1/minor | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD264 | Asset | Power distribution | Route floodlighting | Long hot, dry summer | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 4/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD265 | Asset | Power distribution | Route floodlighting | Long wet winter/spring | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD266 | Asset | Power distribution | Route floodlighting | Heavy rain/cloudburst | Direct | Excess water can damage structures, luminaires and cables | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Increasing intense rainfall increases the risk of damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD267 | Asset | Power distribution | Route floodlighting | High soil moisture | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current conditions | 2/minor | 3/minor | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD268 | Asset | Power distribution | Route floodlighting | Low soil moisture | Direct | Low soil moisture content can affect structures and increase earthing resistance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD269 | Asset | Power distribution | Route floodlighting | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | High | Current typical flood levels are known and accounted for | 2/minor | 3/minor | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD27 | Asset | Power distribution | LV cables | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Low | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD270 | Asset | Power distribution | Route floodlighting | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD271 | Asset | Power distribution | HV cable route | Long hot, dry summer | Indirect | Change in ground conditions can affect cable routes | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Low | Mitigations designed into overall electrical system | 4/moderate | 6/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD272 | Asset | Power distribution | Route floodlighting | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD273 | Asset | Power distribution | Route floodlighting | High winds | Direct | Excess wind loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is exposed | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | High wind speeds are likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD274 | Asset | Power distribution | Route floodlighting | Storms | Direct | Storms can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Storm frequency and severity is likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding | Risk to transport from high and low temperatures, high winds, lightning
PD275 | Asset | Power distribution | HV cable route | Long wet winter/spring | Indirect | Change in ground conditions can affect cable routes | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 3/minor | Low | Mitigations designed into overall electrical system | 3/minor | 6/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD276 | Asset | Power distribution | Siding lighting | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | High | Current typical flood levels are known and accounted for | 2/minor | 3/minor | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD277 | Asset | Power distribution | Siding lighting | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD278 | Asset | Power distribution | Siding lighting | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD279 | Asset | Power distribution | Tunnel heating equipment | High average rainfall over several days | Indirect | Excess water penetrating the tunnel lining can cause arcing and damage to electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Low | Event unlikely, current controls mostly effective | 2/minor | 3/minor | Low | Increasing ground water levels are likely to affect tunnel contents | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD28 | Asset | Power distribution | LV cables | Erosion | Direct | Erosion can expose surface and buried cables | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is incorporated into earthworks | 4/moderate | Medium | Current mitigations generally effective | 4/moderate | 6/moderate | Low | Increased risk of exposure of assets and consequential damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD280 | Asset | Power distribution | Tunnel heating equipment | High average rainfall over season | Indirect | Excess water penetrating the tunnel lining can cause arcing and damage to electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Low | Event unlikely, current controls mostly effective | 2/minor | 3/minor | Low | Increasing ground water levels are likely to affect tunnel contents | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD281 | Asset | Power distribution | Tunnel heating equipment | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | High | Current typical flood levels are known and accounted for | 2/minor | 3/minor | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD282 | Asset | Power distribution | AC power supply conditioning | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the severity will be location specific depending on rainfall patterns | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD283 | Asset | Power distribution | HV cable route | Heavy rain/cloudburst | Direct | Change in ground conditions can affect cable routes | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Event unlikely, current controls mostly effective | 3/minor | 4/moderate | Low | Increasing intense rainfall increases the risk of damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD284 | Asset | Power distribution | Tunnel heating equipment | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD285 | Asset | Power distribution | Tunnel lighting | Ice/Hail | Direct | Ice forming in tunnels can damage equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Current controls are mostly effective | 2/minor | 1/minor | Low | Incidence of ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD286 | Asset | Power distribution | Tunnel lighting | High average rainfall over several days | Indirect | Excess water penetrating the tunnel lining can cause arcing and damage to electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Low | Event unlikely, current controls mostly effective | 2/minor | 3/minor | Low | Increasing ground water levels are likely to affect tunnel contents | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD287 | Asset | Power distribution | Tunnel lighting | High average rainfall over season | Indirect | Excess water penetrating the tunnel lining can cause arcing and damage to electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Low | Event unlikely, current controls mostly effective | 2/minor | 3/minor | Low | Increasing ground water levels are likely to affect tunnel contents | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD288 | Asset | Power distribution | Tunnel lighting | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | High | Current typical flood levels are known and accounted for | 2/minor | 3/minor | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD289 | Asset | Power distribution | Tunnel lighting | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD29 | Asset | Power distribution | LV cables | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 4/moderate | Low | Unlikely but can have devastating effects | 4/moderate | 4/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD290 | Asset | Power distribution | Train shore supplies - 3 phase 400V AC and single phase 850V AC (Excl. 750 V DC supplies) | Snow | Direct | Excess water can provide a low-resistance path between exposed terminals, and snow build-up can physically prevent the use of the shore supply | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Shore supplies generally used in non-operational times and places | 2/minor | 1/minor | Low | Incidence of snow/ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD291 | Asset | Power distribution | Train shore supplies - 3 phase 400V AC and single phase 850V AC (Excl. 750 V DC supplies) | Ice/Hail | Direct | Excess water can provide a low-resistance path between exposed terminals, and snow build-up can physically prevent the use of the shore supply | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Shore supplies generally used in non-operational times and places | 2/minor | 1/minor | Low | Incidence of ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD292 | Asset | Power distribution | Train shore supplies - 3 phase 400V AC and single phase 850V AC (Excl. 750 V DC supplies) | Snow/ice | Direct | Excess water can provide a low-resistance path between exposed terminals, and snow build-up can physically prevent the use of the shore supply | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Shore supplies generally used in non-operational times and places | 2/minor | 1/minor | Low | Incidence of snow/ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD293 | Asset | Power distribution | Train shore supplies - 3 phase 400V AC and single phase 850V AC (Excl. 750 V DC supplies) | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD294 | Asset | Power distribution | HV cable route | High average rainfall over several days | Direct | Change in ground conditions can affect cable routes | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Current controls mostly effective | 4/moderate | 6/moderate | Low | Increasing ground water levels are likely to affect buried and part-buried assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD295 | Asset | Power distribution | Train shore supplies - 3 phase 400V AC and single phase 850V AC (Excl. 750 V DC supplies) | Heavy rain/cloudburst | Direct | Excess water can provide a low-resistance path between exposed terminals | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Shore supplies generally used in non-operational times and places | 4/moderate | 6/moderate | Low | Increasing intense rainfall increases the risk of damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD296 | Asset | Power distribution | Train shore supplies - 3 phase 400V AC and single phase 850V AC (Excl. 750 V DC supplies) | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD297 | Asset | Power distribution | Train shore supplies - 3 phase 400V AC and single phase 850V AC (Excl. 750 V DC supplies) | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD298 | Asset | Power distribution | Train shore supplies - 3 phase 400V AC and single phase 850V AC (Excl. 750 V DC supplies) | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | Medium | Shore supplies generally used in non-operational times and places | 2/minor | 3/minor | Low | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD299 | Asset | Power distribution | Shore supplies (line side) | Snow | Direct | Excess water can provide a low-resistance path between exposed terminals, and snow build-up can physically prevent the use of the shore supply | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Shore supplies generally used in non-operational times and places | 2/minor | 1/minor | Low | Incidence of snow/ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD30 | Asset | Power distribution | LV cables | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 4/moderate | High | More likely than a direct strike, but far easier to repair | 4/moderate | 6/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD300 | Asset | Power distribution | Shore supplies (line side) | Ice/Hail | Direct | Excess water can provide a low-resistance path between exposed terminals, and snow build-up can physically prevent the use of the shore supply | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Shore supplies generally used in non-operational times and places | 2/minor | 1/minor | Low | Incidence of ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD301 | Asset | Power distribution | Shore supplies (line side) | Snow/ice | Direct | Excess water can provide a low-resistance path between exposed terminals, and snow build-up can physically prevent the use of the shore supply | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition. | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Shore supplies generally used in non-operational times and places | 2/minor | 1/minor | Low | Incidence of snow/ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD302 | Asset | Power distribution | Shore supplies (line side) | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition. | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD303 | Asset | Power distribution | Shore supplies (line side) | Heavy rain/cloudburst | Direct | Excess water can provide a low-resistance path between exposed terminals | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Shore supplies generally used in non-operational times and places | 4/moderate | 6/moderate | Low | Increasing intense rainfall increases the risk of damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD304 | Asset | Power distribution | Shore supplies (line side) | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD305 | Asset | Power distribution | HV cable route | High average rainfall over season | Direct | Change in ground conditions can affect cable routes | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Current controls mostly effective | 2/minor | 3/minor | Low | Increasing ground water levels are likely to affect buried and part-buried assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD306 | Asset | Power distribution | Shore supplies (line side) | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD307 | Asset | Power distribution | Shore supplies (line side) | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | Medium | Shore supplies generally used in non-operational times and places | 2/minor | 3/minor | Low | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD308 | Asset | Power distribution | HV cable route/ HV URX/UTX | Flooding | Direct | Flooding can dislodge and damage cable routes | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Low | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD309 | Asset | Power distribution | HV/LV and 3rd rail cables and earth bonds | Erosion | Direct | Erosion can expose surface and buried cable routes | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is incorporated into earthworks | 4/moderate | Medium | Mitigations designed into overall electrical system | 4/moderate | 6/moderate | Low | Increased risk of exposure of assets and consequential damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD31 | Asset | Power distribution | LV switchgear | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD310 | Asset | Power distribution | HV URX/UTX | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD311 | Asset | Power distribution | HV URX/UTX | Heavy rain/cloudburst | Direct | Excess water can dislodge and damage cable routes and contents | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 1/minor | Medium | Event unlikely, current controls mostly effective | 1/minor | 2/minor | Low | Increasing intense rainfall increases the risk of damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD312 | Asset | Power distribution | HV URX/UTX | High average rainfall over several days | Direct | Excess water can dislodge and damage cable routes and contents | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Current controls mostly effective | 4/moderate | 6/moderate | Low | Increasing ground water levels are likely to affect buried and part-buried assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD313 | Asset | Power distribution | HV URX/UTX | High average rainfall over season | Direct | Excess water can dislodge and damage cable routes and contents | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Current controls mostly effective | 2/minor | 3/minor | Low | Increasing ground water levels are likely to affect buried and part-buried assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD314 | Asset | Power distribution | AC power supply conditioning | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 6/moderate | Low | Unlikely but can have devastating effects | 6/moderate | 6/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD315 | Asset | Power distribution | SCADA (all) | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 4/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD316 | Asset | Power distribution | SCADA (all) | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD317 | Asset | Power distribution | SCADA (all) | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD318 | Asset | Power distribution | SCADA (all) | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD319 | Asset | Power distribution | SCADA (all) | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | High | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD32 | Asset | Power distribution | LV switchgear | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Asset is generally capable of withstanding current range of temperatures | 4/moderate | 6/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD320 | Asset | Power distribution | DC grid supply point/Functional Supply Points | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Extreme weather can cause power supplies to fluctuate, but generally capable of withstanding high temperatures | Assuming current National Grid trends continue | Risk to transport from high and low temperatures, high winds, lightning
PD321 | Asset | Power distribution | DC grid supply point | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD322 | Asset | Power distribution | DC grid supply point | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD323 | Asset | Power distribution | DC grid supply point | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD324 | Asset | Power distribution | DC grid supply point | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 8/moderate | Low | Unlikely but can have devastating effects | 8/moderate | 8/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD325 | Asset | Power distribution | AC power supply conditioning | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 6/moderate | High | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD326 | Asset | Power distribution | DC grid supply point | Lightning | Interdependency (us on them) | Impulse from a lightning strike elsewhere on the network can cause fluctuations of the electrical supply | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a National Grid dependency across the country | 6/moderate | Medium | Unlikely. Mitigations generally effective, where applied | 9/moderate | 12/major | Low | Lightning strikes across the country will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD327 | Asset | Power distribution | 3rd Rail DC switchgear & disconnectors | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 4/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD328 | Asset | Power distribution | 3rd Rail DC/ HV switchgear | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 6/moderate | 9/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD329 | Asset | Power distribution | 3rd Rail DC switchgear & disconnectors | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD33 | Asset | Power distribution | Auxiliary transformer | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD330 | Asset | Power distribution | 3rd rail DC switchgear & disconnectors | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 8/moderate | Low | Unlikely but can have devastating effects | 8/moderate | 8/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD331 | Asset | Power distribution | 3rd rail DC switchgear & disconnectors | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | High | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD332 | Asset | Power distribution | 3rd rail DC switchgear & disconnectors | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD333 | Asset | Power distribution | 3rd rail HV cables, transformer/ rectifier | Extreme hot days | Cumulative | High temperatures degrade cable performance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 6/moderate | 6/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD334 | Asset | Power distribution | HV power system protection | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 4/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD335 | Asset | Power distribution | 3rd rail HV cables, transformer/ rectifier | Heat wave | Cumulative | High temperatures degrade cable performance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 6/moderate | 9/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD336 | Asset | Power distribution | 3rd rail HV cables | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD337 | Asset | Power distribution | 3rd rail HV cables | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Low | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD338 | Asset | Power distribution | 3rd rail HV cables | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 8/moderate | Low | Unlikely but can have devastating effects | 8/moderate | 8/moderate | low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD339 | Asset | Power distribution | 3rd rail HV cables | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 4/moderate | High | More likely than a direct strike, but far easier to repair | 4/moderate | 6/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD34 | Asset | Power distribution | LV switchgear | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD340 | Asset | Power distribution | 3rd rail DC switchgear & disconnectors | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 6/moderate | 6/moderate | low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD341 | Asset | Power distribution | 3rd rail HV switchgear | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 6/moderate | 9/moderate | low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD342 | Asset | Power distribution | 3rd rail HV switchgear | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulating media | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD343 | Asset | Power distribution | 3rd rail HV switchgear & transformer/ rectifier | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD344 | Asset | Power distribution | HV power system protection | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD345 | Asset | Power distribution | 3rd rail HV switchgear | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 8/moderate | Low | Unlikely but can have devastating effects | 8/moderate | 8/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD346 | Asset | Power distribution | 3rd rail HV switchgear | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | High | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD347 | Asset | Power distribution | 3rd rail HV cables, transformer/ rectifier | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 6/moderate | 9/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD348 | Asset | Power distribution | 3rd rail transformer/ rectifier | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD349 | Asset | Power distribution | 3rd rail transformer/ rectifier | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 8/moderate | Low | Unlikely but can have devastating effects | 8/moderate | 8/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD35 | Asset | Power distribution | LV switchgear | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 6/moderate | Low | Unlikely but can have devastating effects | 6/moderate | 6/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD350 | Asset | Power distribution | 3rd rail transformer/ rectifier | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | High | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD351 | Asset | Power distribution | Conductor rail heating | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of rails to which this equipment is attached | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Low | Asset is generally capable of withstanding current range of temperatures | 2/minor | 3/minor | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD352 | Asset | Power distribution | Conductor rail heating | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | High | Current typical flood levels are known and accounted for | 2/minor | 3/minor | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD353 | Asset | Power distribution | HV power system protection | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 6/moderate | Low | Unlikely but can have devastating effects | 6/moderate | 6/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD354 | Asset | Power distribution | Conductor rail heating | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD355 | Asset | Power distribution | Conductor rail heating | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 3/minor | High | More likely than a direct strike, but far easier to repair | 3/minor | 6/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD356 | Asset | Power distribution | Earthing/bonding | Extreme hot days | Direct | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 3/minor | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 3/minor | 3/minor | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD357 | Asset | Power distribution | Earthing/bonding | Heat wave | Direct | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 3/minor | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 3/minor | 3/minor | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD358 | Asset | Power distribution | Earthing/bonding | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD359 | Asset | Power distribution | Earthing/bonding | Low soil moisture | Direct | Low soil moisture content can increase earthing resistance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 3/minor | Low | This issue often goes undetected | 3/minor | 6/moderate | Low | Effects of low soil moisture will manifest more often and for longer periods | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD36 | Asset | Power distribution | LV switchgear | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | High | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD360 | Asset | Power distribution | Changeover panels | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD361 | Asset | Power distribution | Changeover panels | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD362 | Asset | Power distribution | Changeover panels | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD37 | Asset | Power distribution | Non-traction HV switchgear | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 4/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD38 | Asset | Power distribution | Non traction HV switchgear | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD39 | Asset | Power distribution | Non traction HV switchgear | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulating media | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 3/minor | Low | Asset is generally capable of withstanding current range of temperatures | 6/moderate | 9/moderate | Low | Asset is generally capable of withstanding temperature fluctuations, but there is a known failure mode | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD40 | Asset | Power distribution | Non traction HV switchgear | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Low | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD41 | Asset | Power distribution | Non traction HV switchgear | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 4/moderate | Low | Unlikely but can have devastating effects | 4/moderate | 4/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity. | Risk to transport from high and low temperatures, high winds, lightning
PD42 | Asset | Power distribution | Non traction HV switchgear | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | Medium | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Low | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD43 | Asset | Power distribution | Principal supply points | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 4/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD44 | Asset | Power distribution | Auxiliary transformer | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risk to transport from high and low temperatures, high winds, lightning
PD45 | Asset | Power distribution | Principal supply points | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD46 | Asset | Power distribution | Principal supply points | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 3/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 3/minor | 6/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD47 | Asset | Power distribution | Principal supply points | Low soil moisture | Direct | Low soil moisture content can increase earthing resistance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 3/minor | Low | This issue often goes undetected | 3/minor | 6/moderate | Low | Effects of low soil moisture will manifest more often and for longer periods | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD48 | Asset | Power distribution | Principal supply points | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD49 | Asset | Power distribution | Principal supply points | Erosion | Direct | Erosion can expose surface and buried cables and increase earthing resistances | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 3/minor | Medium | Current asset condition known, mitigations generally effective | 3/minor | 6/moderate | Low | Controls are effective, but damage to these assets will be service-affecting until repaired or replaced | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD50 | Asset | Power distribution | Principal supply points | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 6/moderate | Low | Unlikely but can have devastating effects | 6/moderate | 6/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD51 | Asset | Power distribution | Principal supply points | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | High | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD52 | Asset | Power distribution | Principal supply points | High winds | Direct | Excess wind loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is exposed | 6/moderate | Medium | Structures are designed to withstand current weather extremes | 6/moderate | 9/moderate | Low | High wind speeds are likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD53 | Asset | Power distribution | Principal supply points | Storms | Direct | Storms can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 6/moderate | Medium | Structures are designed to withstand current weather extremes | 6/moderate | 9/moderate | Low | Storm frequency and severity is likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning | Risks to infrastructure services from river, surface water and groundwater flooding
PD54 | Asset | Power distribution | Remote monitoring interfaces (plant) | Extreme hot days | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 2/minor | 2/minor | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD55 | Asset | Power distribution | Auxiliary transformer | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 6/moderate | Low | Unlikely but can have devastating effects | 6/moderate | 6/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD56 | Asset | Power distribution | Remote monitoring interfaces (plant) | Heat wave | Cumulative | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 2/minor | 3/minor | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD57 | Asset | Power distribution | Remote monitoring interfaces (plant) | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD58 | Asset | Power distribution | Remote monitoring interfaces (plant) | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD59 | Asset | Power distribution | Remote monitoring interfaces (plant) | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD60 | Asset | Power distribution | Solar and wind trackside power supply | Extreme hot days | Direct | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 2/minor | 2/minor | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD61 | Asset | Power distribution | Solar and wind trackside power supply | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD62 | Asset | Power distribution | Solar and wind trackside power supply | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD63 | Asset | Power distribution | Solar and wind trackside power supply | Erosion | Direct | Erosion can expose surface equipment and buried cables, and increase earthing resistances | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 4/moderate | Medium | Current asset condition known, mitigations generally effective | 4/moderate | 6/moderate | Low | Increased risk of exposure of assets and consequential damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action. | Risks to infrastructure services from river, surface water and groundwater flooding
PD64 | Asset | Power distribution | Solar and wind trackside power supply | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD65 | Asset | Power distribution | Solar and wind trackside power supply | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD66 | Asset | Power distribution | Auxiliary transformer | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 6/moderate | High | More likely than a direct strike, but far easier to repair | 6/moderate | 9/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD67 | Asset | Power distribution | Solar and wind trackside power supply | Storms | Direct | Storms can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Storm frequency and severity is likely to increase | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding | Risk to transport from high and low temperatures, high winds, lightning
PD68 | Asset | Power distribution | Standby generators (fixed position) | Extreme hot days | Direct | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 4/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD69 | Asset | Power distribution | Standby generators (fixed position) | Heat wave | Direct | High temperatures affect electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD70 | Asset | Power distribution | Standby generators (fixed position) | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of moving parts | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD71 | Asset | Power distribution | Standby generators (fixed position) | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD72 | Asset | Power distribution | UPS integrated into distribution system | Extreme hot days | Cumulative | High temperatures affect electrical equipment and degrade batteries | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Low | Current controls mostly effective, further controls in development | 8/moderate | 10/major | Low | Battery performance and life are known to degrade predictably with high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD73 | Asset | Power distribution | UPS integrated into distribution system | Heat wave | Cumulative | High temperatures affect electrical equipment and degrade batteries | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Medium | Current controls mostly effective, further controls in development | 9/moderate | 12/major | Medium | Increasing temperatures will increase degradation of batteries | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD74 | Asset | Power distribution | UPS integrated into distribution system | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 3/minor | Medium | Current controls are mostly effective, new controls in development | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD75 | Asset | Power distribution | UPS integrated into distribution system | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | High | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Medium | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD76 | Asset | Power distribution | UPS integrated into distribution system | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD77 | Asset | Power distribution | Battery & charger | Extreme hot days | Cumulative | High temperatures degrade batteries | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Low | Current controls mostly effective, further controls in development | 8/moderate | 10/major | Low | Battery performance and life are known to degrade predictably with high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD78 | Asset | Power distribution | UPS integrated into distribution system | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | High | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD79 | Asset | Power distribution | Cable: signalling cable >120V | Extreme hot days | Direct | High temperatures degrade cable performance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 4/moderate | Low | Asset is generally capable of withstanding high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD80 | Asset | Power distribution | Cables: signalling cable >120V; 1500V DC and HV cables | Heat wave | Direct | High temperatures degrade cable performance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current asset condition is known and generally capable of withstanding current range of high temperatures | 4/moderate | 6/moderate | Low | Increasing temperatures will increase degradation of electrical equipment | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD81 | Asset | Power distribution | Cable: signalling cable >120V | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Asset is generally capable of withstanding current range of temperatures | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD82 | Asset | Power distribution | Cables: signalling cable >120V; 1500V DC and HV cables | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Low | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD83 | Asset | Power distribution | Cables: signalling cable >120V; 1500V DC and HV cables | Erosion | Direct | Erosion can expose surface and buried cables | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is incorporated into earthworks | 4/moderate | Medium | Current mitigations generally effective | 4/moderate | 6/moderate | Low | Increased risk of exposure of assets and consequential damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD84 | Asset | Power distribution | Cable: signalling cable >120V | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 4/moderate | Low | Unlikely but can have devastating effects | 4/moderate | 4/moderate | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD85 | Asset | Power distribution | Cable: signalling cable >120V | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 4/moderate | High | More likely than a direct strike, but far easier to repair | 4/moderate | 6/moderate | Medium | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD86 | Asset | Power distribution | Lighting support structure | Ice/Hail | Direct | Excess snow and ice loading can damage structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Structures are designed to withstand current weather extremes | 4/moderate | 2/minor | Low | Incidence of ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD87 | Asset | Power distribution | Lighting support structure | Snow/ice | Direct | Snow and ice can affect structure loading | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 1/minor | Low | Incidence of snow/ice/hail is expected to decrease | Assuming current extreme lows persist | Risk to transport from high and low temperatures, high winds, lightning
PD88 | Asset | Power distribution | Battery & charger | Heat wave | Cumulative | High temperatures degrade batteries | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 6/moderate | Medium | Current controls mostly effective, further controls in development | 8/moderate | 10/major | Medium | Asset performance and life are known to degrade with high temperatures | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD89 | Asset | Power distribution | Lighting support structure | Large diurnal temperature range | Direct | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 4/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PD90 | Asset | Power distribution | Lighting support structure | Long hot, dry summer | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 4/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to transport networks from slope and embankment failure | Risk to transport from high and low temperatures, high winds, lightning
PD91 | Asset | Power distribution | Lighting support structure | Long wet winter/spring | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 3/minor | Medium | Structures are designed to withstand current weather extremes | 3/minor | 6/moderate | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD92 | Asset | Power distribution | Lighting support structure | Heavy rain/cloudburst | Direct | Excess water can damage structures, luminaires and cables | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Increasing intense rainfall increases the risk of damage to exposed assets | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD93 | Asset | Power distribution | Lighting support structure | High soil moisture | Direct | Change in ground conditions can affect structures | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD94 | Asset | Power distribution | Lighting support structure | Low soil moisture | Direct | Low soil moisture content can affect structures and increase earthing resistance | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 2/minor | Medium | Structures are designed to withstand current weather extremes | 2/minor | 3/minor | Low | Changes in ground condition will be exaggerated from current norms | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risk to transport from high and low temperatures, high winds, lightning
PD95 | Asset | Power distribution | Lighting support structure | Flooding | Direct | Flooding affects electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the North West and areas where rainfall levels will be higher | 4/moderate | Medium | Current typical flood levels are known and accounted for | 4/moderate | 6/moderate | Low | As flood areas and severities increase, risk of damage to assets increases | Assuming current drainage strategies persist | Risks to infrastructure services from river, surface water and groundwater flooding
PD96 | Asset | Power distribution | Lighting support structure | Erosion | Direct | Erosion can expose structure foundations and buried cables, and increase earthing resistances | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country, particularly in areas where the asset is on earthworks | 2/minor | Medium | Current asset condition known, mitigations generally effective | 2/minor | 3/minor | Low | Increasing erosion increases risk of foundation issues | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
PD97 | Asset | Power distribution | Lighting support structure | Lightning | Direct | A direct lightning strike will damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country although the risk will be higher in areas with more thunderstorms | 2/minor | Low | Unlikely but can have devastating effects | 2/minor | 2/minor | Low | Direct lightning strikes remain unlikely | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD98 | Asset | Power distribution | Lighting support structure | Lightning | Indirect | Impulse from a lightning strike elsewhere on the network can damage electrical equipment | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | This is a risk across the country | 2/minor | Medium | More likely than a direct strike, but far easier to repair | 2/minor | 3/minor | Low | Lightning strikes in a local area will increase | Assuming general increase in storm frequency and severity | Risk to transport from high and low temperatures, high winds, lightning
PD99 | Asset | Power distribution | Battery & charger | Large diurnal temperature range | Cumulative | High temperature variance can lead to rapid expansion and contraction of conductors and insulators | Whole country | Professional Head of Power Distribution HV/LV | Linked to trigger level for investment which is asset condition | There is a risk across the country although the risk will be higher in the South East and areas where the temperature will be higher | 4/moderate | Medium | Current controls are mostly effective, new controls in development | 4/moderate | 6/moderate | Low | Asset is generally capable of withstanding temperature fluctuations | Assuming current manufacturing techniques and materials | Risk to transport from high and low temperatures, high winds, lightning
PLT1 -26 | N/A | Plant | Plant weather and climate change risks have been referenced from a wider risk assessment from this Asset Function. Risks PTL1 - 26 have not been included in this table as they refer to non-asset related risks
PLT27 | Asset | Plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Long wet winter/spring | Direct | N/A | Whole country | Professional Head of Plant & Asset Manager | N/A | Selection of risk do not affect plant because they are either built to cope or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | N/A | N/A | Selection of risk does not affect plant because they are either built to cope, or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | N/A | N/A | N/A | Selection of risk does not affect plant because they are either built to cope, or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | Plant fit for purpose and able to work in selected conditions if supported activity goes ahead | Risks to infrastructure services from river, surface water and groundwater flooding
PLT28 | Asset | Plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Light rain/drizzle | Direct | N/A | Whole country | Professional Head of Plant & Asset Manager | N/A | Selection of risk do not affect plant because they are either built to cope or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | N/A | N/A | Selection of risk does not affect plant because they are either built to cope, or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | N/A | N/A | N/A | Selection of risk does not affect plant because they are either built to cope, or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | Plant fit for purpose and able to work in selected conditions if supported activity goes ahead
PLT29 | Asset | Plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | High average rainfall over several days | Direct | N/A | Whole country | Professional Head of Plant & Asset Manager | N/A | Selection of risk do not affect plant because they are either built to cope or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | N/A | N/A | Selection of risk does not affect plant because they are either built to cope, or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | N/A | N/A | N/A | Selection of risk does not affect plant because they are either built to cope, or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | Plant fit for purpose and able to work in selected conditions if supported activity goes ahead | Risks to infrastructure services from river, surface water and groundwater flooding
PLT30 | Asset | Plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | High average rainfall over season | Direct | N/A | Whole country | Professional Head of Plant & Asset Manager | N/A | Selection of risk do not affect plant because they are either built to cope or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | N/A | N/A | Selection of risk does not affect plant because they are either built to cope, or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | N/A | N/A | N/A | Selection of risk does not affect plant because they are either built to cope, or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | Plant fit for purpose and able to work in selected conditions if supported activity goes ahead | Risks to infrastructure services from river, surface water and groundwater flooding
PLT31 | Asset | Plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Low average rainfall | Direct | N/A | Whole country | Professional Head of Plant & Asset Manager | N/A | Selection of risk do not affect plant because they are either built to cope or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | N/A | N/A | Selection of risk does not affect plant because they are either built to cope, or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | N/A | N/A | N/A | Selection of risk does not affect plant because they are either built to cope, or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | Plant fit for purpose and able to work in selected conditions if supported activity goes ahead
PLT32 | Asset | Plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Low soil moisture | Indirect | N/A | Whole country | Professional Head of Plant & Asset Manager | N/A | Selection of risk do not affect plant because they are either built to cope or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | N/A | N/A | Selection of risk does not affect plant because they are either built to cope, or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | N/A | N/A | N/A | Selection of risk does not affect plant because they are either built to cope, or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | Plant fit for purpose and able to work in selected conditions if supported activity goes ahead | Risk to transport from high and low temperatures, high winds, lightning
PLT33 | Asset | Plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Erosion | Indirect | N/A | Whole country | Professional Head of Plant & Asset Manager | N/A | Selection of risk do not affect plant because they are either built to cope or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | N/A | N/A | Selection of risk does not affect plant because they are either built to cope, or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | N/A | N/A | N/A | Selection of risk does not affect plant because they are either built to cope, or the activity which they support would be cancelled independent of plant fitness for purpose (plant assumed to be fit) | Plant fit for purpose and able to work in selected conditions if supported activity goes ahead | Risks to infrastructure services from river, surface water and groundwater flooding
PLT34 | Asset | On-track plant & mobile plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Extreme hot days | Direct | Machine engine overheats leading to machine fire risk | Whole country | Professional Head of Plant & Asset Manager | Engine overheat limit specific to engine type; fire prevention requirements set in standard | - Hazard is specifically mentioned in clause 1.5.6 Fire of Machinery Directive 2006/42/EC - Clause 5.30 Fire prevention in RIS-1530-PLT issue 6 - Rail Industry Standard for Technical Requirements for On-Track Plant and their associated Equipment and Trolleys - Hazard is not covered in BS EN ISO 474-1-2006+A6-2019. Earth moving machinery - Fire prevention specifically covered in: (1) BS EN 15746-2:2010+A1:2011 - Railway applications - Track - Road rail machines and their associated equipment - Part 2: General Safety requirements (2) BS EN 15954-2:2013 - Railway applications - Track - Trailers and associated equipment. General safety requirements (3) BS EN 15955-2:2013 - Railway applications. Tracks Demountable machines and associated equipment. General safety requirements | 2/minor | Medium | Hazard is specifically covered in standards | 2/minor | 2/minor | Medium | Temperature increase is within current working temperature of engines. In addition there is confidence from operational experience in much warmer countries | Track more likely to be affected before machine breakdown occurs | Risk to transport from high and low temperatures, high winds, lightning
PLT35 | Asset | On-track plant & mobile plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Heat wave | Direct | Machine engine overheats leading to machine fire risk | Whole country | Professional Head of Plant & Asset Manager | Engine overheat limit specific to engine type; fire prevention requirements set in standard | - Hazard is specifically mentioned in clause 1.5.6 Fire of Machinery Directive 2006/42/EC - Clause 5.30 Fire prevention in RIS-1530-PLT issue 6 - Rail Industry Standard for Technical Requirements for On-Track Plant and their associated Equipment and Trolleys - Hazard is not covered in BS EN ISO 474-1-2006+A6-2019. Earth moving machinery - Fire prevention specifically covered in: (1) BS EN 15746-2:2010+A1:2011 - Railway applications - Track - Road rail machines and their associated equipment - Part 2: General Safety requirements (2) BS EN 15954-2:2013 - Railway applications - Track - Trailers and associated equipment. General safety requirements (3) BS EN 15955-2:2013 - Railway applications. Tracks Demountable machines and associated equipment. General safety requirements | 2/minor | Medium | Hazard is specifically covered in standards | 2/minor | 2/minor | Medium | Temperature increase is within current working temperature of engines. In addition there is confidence from operational experience in much warmer countries | Track more likely to be affected before machine breakdown occurs | Risk to transport from high and low temperatures, high winds, lightning
PLT36 | Asset | On-track plant & mobile plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Higher average temperature | Direct | Machine engine overheats leading to machine fire risk | Whole country | Professional Head of Plant & Asset Manager | Engine overheat limit specific to engine type; fire prevention requirements set in standard | - Hazard is specifically mentioned in clause 1.5.6 Fire of Machinery Directive 2006/42/EC - Clause 5.30 Fire prevention in RIS-1530-PLT issue 6 - Rail Industry Standard for Technical Requirements for On-Track Plant and their associated Equipment and Trolleys. - Hazard is not covered in BS EN ISO 474-1-2006+A6-2019. Earth moving machinery. - Fire prevention specifically covered in: (1) BS EN 15746-2:2010+A1:2011 - Railway applications - Track - Road rail machines and their associated equipment - Part 2: General Safety requirements. (2) BS EN 15954-2:2013 - Railway applications - Track - Trailers and associated equipment. General safety requirements. (3) BS EN 15955-2:2013 - Railway applications. Tracks. Demountable machines and associated equipment. General safety requirements | 2/minor | Medium | Hazard is specifically covered in standards | 2/minor | 2/minor | Medium | Temperature increase is within current working temperature of engines. In addition there is confidence from operational experience in much warmer countries | Track more likely to be affected before machine breakdown occurs | Risk to transport from high and low temperatures, high winds, lightning
PLT37 | Asset | On-track plant & mobile plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Long hot, dry summer | Direct | Machine engine overheats leading to machine fire risk | Whole country | Professional Head of Plant & Asset Manager | Engine overheat limit specific to engine type; fire prevention requirements set in standard | - Hazard is specifically mentioned in clause 1.5.6 Fire of Machinery Directive 2006/42/EC - Clause 5.30 Fire prevention in RIS-1530-PLT issue 6 - Rail Industry Standard for Technical Requirements for On-Track Plant and their associated Equipment and Trolleys. - Hazard is not covered in BS EN ISO 474-1-2006+A6-2019. Earth moving machinery. - Fire prevention specifically covered in: (1) BS EN 15746-2:2010+A1:2011 - Railway applications - Track - Road rail machines and their associated equipment - Part 2: General Safety requirements. (2) BS EN 15954-2:2013 - Railway applications - Track - Trailers and associated equipment. General safety requirements. (3) BS EN 15955-2:2013 - Railway applications. Tracks. Demountable machines and associated equipment. General safety requirements | 2/minor | Medium | Hazard is specifically covered in standards | 2/minor | 2/minor | Medium | Temperature increase is within current working temperature of engines. In addition there is confidence from operational experience in much warmer countries | Track more likely to be affected before machine breakdown occurs | Risk to transport from high and low temperatures, high winds, lightning
PLT38 | Asset | On-track plant & mobile plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Extreme hot days | Direct | Thermal stressing leading to shorter component lifespan and higher consumables (oil, water, wiring) | Whole country | Professional Head of Plant & Asset Manager | None | Decision threshold criteria does not apply, diurnal temperature range is already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes | 2/minor | Medium | Operational & Storage thermal duty cycle already forms part of specification writing process | 2/minor | 2/minor | Medium | Operational & Storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables (2) Plant Supplier hires machine that is fit for purpose and reflects increased cost in hire rate (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT39 | Asset | On-track plant & mobile plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Heat wave | Direct | Thermal stressing leading to shorter component lifespan and higher consumables (oil, water, wiring) | Whole country | Professional Head of Plant & Asset Manager | None | Decision threshold criteria does not apply, diurnal temperature range is already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes | 2/minor | Medium | Operational & Storage thermal duty cycle already forms part of specification writing process | 2/minor | 2/minor | Medium | Operational & Storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables (2) Plant Supplier hires machine that is fit for purpose and reflects increased cost in hire rate (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT40 | Asset | On-track plant & mobile plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Higher average temperature | Direct | Thermal stressing leading to shorter component lifespan and higher consumables (oil, water, wiring) | Whole country | Professional Head of Plant & Asset Manager | None | Decision threshold criteria does not apply, diurnal temperature range is already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes | 2/minor | Medium | Operational & Storage thermal duty cycle already forms part of specification writing process | 2/minor | 2/minor | Medium | Operational & Storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables (2) Plant Supplier hires machine that is fit for purpose and reflects increased cost in hire rate (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT41 | Asset | On-track plant & mobile plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Long hot, dry summer | Direct | Thermal stressing leading to shorter component lifespan and higher consumables (oil, water, wiring) | Whole country | Professional Head of Plant & Asset Manager | None | Decision threshold criteria does not apply, diurnal temperature range is already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes | 2/minor | Medium | Operational & Storage thermal duty cycle already forms part of specification writing process | 2/minor | 2/minor | Medium | Operational & Storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables (2) Plant Supplier hires machine that is fit for purpose and reflects increased cost in hire rate (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT42 | Asset | On-track plant & mobile plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Large diurnal temperature range | Direct | Thermal stressing leading to shorter component lifespan and higher consumables (oil, water, wiring) | Whole country | Professional Head of Plant & Asset Manager | None | Decision threshold criteria does not apply, diurnal temperature range is already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes | 2/minor | Medium | Operational & Storage thermal duty cycle already forms part of specification writing process | 2/minor | 2/minor | Medium | Operational & Storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables (2) Plant Supplier hires machine that is fit for purpose and reflects increased cost in hire rate (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT43 | Asset | On-track plant & mobile plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Lightning | Direct | Bonding unable to safely channel lightning to the rail causing electrocution and damage to asset | Whole country | Professional Head of Plant & Asset Manager | Lightning warning | - Hazard is specifically mentioned in clause 1.5.16 Lightning of Machinery Directive 2006/42/EC - Hazard is not covered in BS EN ISO 474-1-2006+A6-2019. Earth moving machinery. - Hazard not covered in: (1) BS EN 15746-2:2010+A1:2011 - Railway applications - Track - Road rail machines and their associated equipment - Part 2: General Safety requirements (2) BS EN 15954-2:2013 - Railway applications - Track - Trailers and associated equipment. General safety requirements. (3) BS EN 15955-2:2013 - Railway applications. Tracks Demountable machines and associated equipment. General safety requirements (4) BS EN 13977:2011 - Railway applications. Track. Safety requirements for portable machines and trolleys for construction and maintenance | 3/minor | Medium | Reliance on plant converter/ manufacturer and supplier to have devised an engineering means to address lightning | 3/minor | 3/minor | Low | Network Rail shift procedure is most robust defence because this greatly reduces the risk of occurrence Most common way of dealing with lightning is to avoid it and where possible design for it (as done with buildings and aircraft). Means of making plant lightning proof to be investigated - Action 2 UKCP09 technical note - Future changes in lightning from the UKCP09 ensemble of regional climate model projections. Section 9 Summary...'increases in the number of lightning days are projected for all four seasons across the whole of the UK' | (1)The frequency of this risk changes based on regions and season (2) Network Rail Shift planning process includes consideration of extreme weather condition. Therefore mobile plant is unlikely to be working because safety concern for operators should lead to shift cancellation (3) If discovered and deemed practical, means of making plant lightning proof will lead to amendment of NR shift planning process | Risk to transport from high and low temperatures, high winds, lightning
PLT44 | Asset | On-track plant & mobile plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | High winds | Direct | Mobile Elevated Mobile Platforms(MEWPs) and cranes can not work in excessive wind conditions - MEWPs windspeed exceeding 28mph (12.5m/s) - Manbaskets windspeed exceeding 25mph (11.5m/s) - Mobile Cranes normally 31mph (13.5m/s) | Whole country | Professional Head of Plant & Asset Manager | Wind speed | Hazard is specifically covered for MEWPs in BS EN 280: 2013+A1:2015 (Mobile Elevated working platforms, design calculations. stability criteria. construction. safety. examinations and tests). 28mph (12.5m/s) - BS 7121(Code of practice for safe use of cranes) Manbaskets windspeed exceeding 25mph (11.5m/s) - Mobile Cranes normally 31mph (13.5m/s) - Duty charts should specify from each manufacturer | 4/moderate | Medium | There is an existing stablished process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure Mobile or On-Track Plant MEWPs normally work alone and are more susceptible to wind loading unlike OTMs which are normally permanently couple to other non-MEWP in working mode | 4/moderate | 4/moderate | Medium | There is an existing process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure NR/GN/ESD23 Issue 1,'Climate Change Projections' Section 11 -Wind. Conclusion: - Global projections over the UK shows increases in near surface wind speeds in the 2nd half of the 21st Century, - For the winter season, when more significant impacts of wind are experience this is accompanied by an increase in frequency of winter storms over the UK, and - That the increase in wind speeds is modest compared to interannual variability | Network Rail procedure adhered to and improved as part of overall climate change and sustainability programmes Modest wind speed increase does not require increase in current working wind speed limit | Risk to transport from high and low temperatures, high winds, lightning
PLT45 | Asset | On-track plant & mobile plant | Road rail vehicle, demountable machines, trailers, trolleys, attachments with 2 or more rail wheels non-rail mobile plant | Storms | Interdependency (them on us) | Access to on track plan will be limited unless operators navigate storms safely which is highly unlikely because the normal procedure is to cancel such shifts | Whole country | Professional Head of Plant & Asset Manager | Storm warning | On track plant can work in storms but may not be able to because of risk of railway furniture striking the workforce( a track issue). It is especially unsafe when lifting or transporting assets | 2/minor | Medium | There is an existing stablished process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure | 2/minor | 2/minor | Medium | There is an existing process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure NR/GN/ESD23 Issue 1,'Climate Change Projections' Section 8.3, 'Regulator guidance for storm surge allowances' Climate change will lead to greater coastal erosion and flooding impacts due to increases in the frequency and intensity of storm events and greater coastal water depths from sea level rise | Network Rail procedure adhered to and improved as part of overall climate change and sustainability programmes Track WRCCA has addressed the risk of storms | Risks to infrastructure services from river, surface water and groundwater flooding | Risk to transport from high and low temperatures, high winds, lightning
PLT46 | Asset | On-track machines | Tampers & regulators, mobile maintenance train, stone blowers, rail grinders, overhead condition renewal fleet, HOPS, breakdown cranes, high output fleet, snow fleet, rail head treatment train, snow & ice treatment train | Extreme hot days | Direct | Machine engine overheats leading to machine fire risk | Whole country | Professional Head of Plant & Asset Manager | Engine overheat limit specific to engine type; fire prevention requirements set in standard | - Hazard is specifically mentioned in clause 1.5.6 Fire of Machinery Directive 2006/42/EC - Hazard is not covered in RIS-1702-PLT Issue 2 (Rail Industry Standard for the Design of On-Track Machines in Travelling and Working Mode.) but is covered in referenced BS EN 14033 -2-2017 (Railway application - Track - Railbound construction and maintenance machine Part 2.) - Hazard is not covered in BS EN ISO 474-1-2006+A6-2019. Earth moving machinery | 2/minor | Medium | Hazard is specifically covered in standards | 2/minor | 2/minor | Medium | Temperature increase is within current working temperature of engines. In addition there is confidence from operational experience in much warmer countries | Based on current machine designs that are international, machinery is assumed to cope with the projected changes in UK. | Risk to transport from high and low temperatures, high winds, lightning
PLT47 | Asset | On-track machines | Tampers & regulators, mobile maintenance train, stone blowers, rail grinders, overhead condition renewal fleet, HOPS, breakdown cranes, high output fleet, snow fleet, rail head treatment train, snow & ice treatment train | Heat wave | Direct | Machine engine overheats leading to machine fire risk | Whole country | Professional Head of Plant & Asset Manager | Engine overheat limit specific to engine type; fire prevention requirements set in standard | - Hazard is specifically mentioned in clause 1.5.6 Fire of Machinery Directive 2006/42/EC - Hazard is not covered in RIS-1702-PLT Issue 2 (Rail Industry Standard for the Design of On-Track Machines in Travelling and Working Mode.) but is covered in referenced BS EN 14033 -2-2017 (Railway application - Track - Railbound construction and maintenance machine Part 2.) - Hazard is not covered in BS EN ISO 474-1-2006+A6-2019. Earth moving machinery | 2/minor | Medium | Hazard is specifically covered in standards | 2/minor | 2/minor | Medium | Temperature increase is within current working temperature of engines. In addition there is confidence from operational experience in much warmer countries | Based on current machine designs that are international, machinery is assumed to cope with the projected changes in UK. | Risk to transport from high and low temperatures, high winds, lightning
PLT48 | Asset | On-track machines | Tampers & regulators, mobile maintenance train, stone blowers, rail grinders, overhead condition renewal fleet, HOPS, breakdown cranes, high output fleet, snow fleet, rail head treatment train, snow & ice treatment train | Long hot, dry summer | Direct | Machine engine overheats leading to machine fire risk | Whole country | Professional Head of Plant & Asset Manager | Engine overheat limit specific to engine type; fire prevention requirements set in standard | - Hazard is specifically mentioned in clause 1.5.6 Fire of Machinery Directive 2006/42/EC - Hazard is not covered in RIS-1702-PLT Issue 2 (Rail Industry Standard for the Design of On-Track Machines in Travelling and Working Mode.) but is covered in referenced BS EN 14033 -2-2017 (Railway application - Track - Railbound construction and maintenance machine Part 2.) - Hazard is not covered in BS EN ISO 474-1-2006+A6-2019. Earth moving machinery | 2/minor | Medium | Hazard is specifically covered in standards | 2/minor | 2/minor | Medium | Temperature increase is within current working temperature of engines. In addition there is confidence from operational experience in much warmer countries | Based on current machine designs that are international, machinery is assumed to cope with the projected changes in UK. | Risk to transport from high and low temperatures, high winds, lightning
PLT49 | Asset | On-track machines | Tampers & regulators, mobile maintenance train, stone blowers, rail grinders, overhead condition renewal fleet, HOPS, breakdown cranes, high output fleet, snow fleet, rail head treatment train, snow & ice treatment train | Higher average temperature | Direct | Machine engine overheats leading to machine fire risk | Whole country | Professional Head of Plant & Asset Manager | Engine overheat limit specific to engine type; fire prevention requirements set in standard | - Hazard is specifically mentioned in clause 1.5.6 Fire of Machinery Directive 2006/42/EC - Hazard is not covered in RIS-1702-PLT Issue 2 (Rail Industry Standard for the Design of On-Track Machines in Travelling and Working Mode.) but is covered in referenced BS EN 14033 -2-2017 (Railway application - Track - Railbound construction and maintenance machine Part 2.) - Hazard is not covered in BS EN ISO 474-1-2006+A6-2019. Earth moving machinery | 2/minor | Medium | Hazard is specifically covered in standards | 2/minor | 2/minor | Medium | Temperature increase is within current working temperature of engines. In addition there is confidence from operational experience in much warmer countries | Based on current machine designs that are international, machinery is assumed to cope with the projected changes in UK. | Risk to transport from high and low temperatures, high winds, lightning
PLT50 | Asset | On-track machines | Tampers & regulators, mobile maintenance train, stone blowers, rail grinders, overhead condition renewal fleet, HOPS, breakdown cranes, high output fleet, snow fleet, rail head treatment train, snow & ice treatment train | Storms | Interdependency (them on us) | Access to on-track machines will be limited unless operators navigate storms safely which is highly unlikely because the normal procedure is to cancel such shifts | Whole country | Professional Head of Plant & Asset Manager | Storm Warning | On-track machinery can not work in storms because of risk of railway furniture striking the workforce. It is especially unsafe when lifting or transporting assets | 1/minor | Medium | There is an existing stablished process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure | 1/minor | 1/minor | Medium | There is an existing stablished process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure NR/GN/ESD23 Issue 1,'Climate Change Projections' Section 8.3, 'Regulator guidance for storm surge allowances' Climate change will lead to greater coastal erosion and flooding impacts due to increases in the frequency and intensity of storm events and greater coastal water depths from sea level rise | Network Rail procedure adhered to and improved as part of overall climate change and sustainability programmes Track WRCCA has addressed the risk of storms | Risks to infrastructure services from river, surface water and groundwater flooding | Risk to transport from high and low temperatures, high winds, lightning
PLT51 | Asset | On-track machines | Tampers & regulators, mobile maintenance train, stone blowers, rail grinders, overhead condition renewal fleet, HOPS, breakdown cranes, high output fleet, snow fleet, rail head treatment train, snow & ice treatment train | Lightning | Direct | Bonding unable to safely channel lightning to the rail causing electrocution and damage to asset | Whole country | Professional Head of Plant & Asset Manager | Lightning warning | - Hazard is specifically mentioned in clause 1.5.16 Lightning of Machinery Directive 2006/42/EC - Hazard is not covered in BS EN ISO 474-1-2006+A6-2019. Earth moving machinery - Hazard not covered in RIS-1702-PLT Issue 2(Rail Industry Standard for the Design of On-Track Machines in Travelling and Working Mode.) or referenced BS EN 14033-2-2017 - Railway application - Track - Railbound construction and maintenance machine Part 2 | 3/minor | Low | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address lightning | 3/minor | 3/minor | Low | Network Rail shift procedure is most robust defence because this greatly reduces the risk of occurrence Most common way of dealing with lightning is to avoid it and where possible design for it (as done with buildings and aircraft). Means of making plant lightning proof to be investigated - Action 2 UKCP09 technical note - Future changes in lightning from the UKCP09 ensemble of regional climate model projections. Section 9 Summary...'increases in the number of lightning days are projected for all four seasons across the whole of the UK' | (1)The frequency of this risk changes based on regions and season (2) Network Rail Shift planning process includes consideration of extreme weather condition. Therefore mobile plant is unlikely to be working because safety concern for operators should lead to shift cancellation (3) If discovered and deemed practical, means of making plant lightening proof will lead to amendment of NR shift planning process | Risk to transport from high and low temperatures, high winds, lightning
PLT52 | Asset | On-track machines - track treatment | Stone blowers | Flooding | Interdependency (them on us) | Machine unable to work because it can not deposit stone onto the track | Whole country | Professional Head of Track & Region | Flood Warning | Not a machine specific hazard | 1/minor | Medium | There is an established process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure | 2/minor | 2/minor | Medium | There is an established process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure. Action 3 NR/GN/ESD23 Issue 1, 'Climate Change Projections Guidance' Section 7 - Flooding…. 'Climate change will significantly increase future flood risk.' | Network Rail procedure adhered to and improved as part of overall climate change and sustainability programmes Track WRCCA has addressed the risk of flooding in order to allow Stone blowers to work | Risks to infrastructure services from river, surface water and groundwater flooding
PLT53 | Asset | On-track machines - track treatment | Rail grinders | Extreme hot days | Interdependency (us on them) | Rail Grinder sets fire to the infrastructure and surrounding area when working | Whole country | Plant Asset Manager & Asset Operator | None | Risk of ignition depends on state of vegetation and level of pollution on the infrastructure within the vicinity of grind spark generated | 2/minor | Medium | This is an existing risk and mitigation has proven to be adequate. Creation of hot by product is inherent to this process and the grinder fleet are all already heavily guarded to prevent sparks igniting lineside vegetation and assets | 2/minor | 2/minor | Medium | This is an existing risk and mitigation has proven to be adequate. Creation of hot by product is inherent to this process and the Grinder fleet are all already heavily guarded to prevent sparks igniting lineside vegetation and assets | Network Rail procedure adhered to and improved as part of overall climate change and sustainability programmes Plant Asset Manager keeps fire suppression system fit for purpose | Risk to transport from high and low temperatures, high winds, lightning
PLT54 | Asset | On-track machines - track treatment | Rail grinders | Heat wave | Interdependency (us on them) | Rail Grinder sets fire to the infrastructure and surrounding area when working | Whole country | Plant Asset Manager & Asset Operator | None | Risk of ignition depends on state of vegetation and level of pollution on the infrastructure within the vicinity of grind spark generated | 2/minor | Medium | This is an existing risk and mitigation has proven to be adequate. Creation of hot by product is inherent to this process and the grinder fleet are all already heavily guarded to prevent sparks igniting lineside vegetation and assets | 2/minor | 2/minor | Medium | This is an existing risk and mitigation has proven to be adequate. Creation of hot by product is inherent to this process and the Grinder fleet are all already heavily guarded to prevent sparks igniting lineside vegetation and assets | Network Rail procedure adhered to and improved as part of overall climate change and sustainability programmes Plant Asset Manager keeps fire suppression system fit for purpose | Risk to transport from high and low temperatures, high winds, lightning
PLT55 | Asset | On-track machines - track treatment | Rail grinders | Long hot, dry summer | Interdependency (us on them) | Rail Grinder sets fire to the infrastructure and surrounding area when working | Whole country | Plant Asset Manager & Asset Operator | None | Risk of ignition depends on state of vegetation and level of pollution on the infrastructure within the vicinity of grind spark generated | 2/minor | Medium | This is an existing risk and mitigation has proven to be adequate. Creation of hot by product is inherent to this process and the grinder fleet are all already heavily guarded to prevent sparks igniting lineside vegetation and assets | 2/minor | 2/minor | Medium | This is an existing risk and mitigation has proven to be adequate. Creation of hot by product is inherent to this process and the Grinder fleet are all already heavily guarded to prevent sparks igniting lineside vegetation and assets | Network Rail procedure adhered to and improved as part of overall climate change and sustainability programmes Plant Asset Manager keeps fire suppression system fit for purpose | Risk to transport from high and low temperatures, high winds, lightning
PLT56 | Asset | On-track machines - track treatment | Rail grinders | Higher average temperature | Interdependency (us on them) | Rail Grinder sets fire to the infrastructure and surrounding area when working | Whole country | Plant Asset Manager & Asset Operator | None | Risk of ignition depends on state of vegetation and level of pollution on the infrastructure within the vicinity of grind spark generated | 2/minor | Medium | This is an existing risk and mitigation has proven to be adequate. Creation of hot by product is inherent to this process and the grinder fleet are all already heavily guarded to prevent sparks igniting lineside vegetation and assets | 2/minor | 2/minor | Medium | This is an existing risk and mitigation has proven to be adequate. Creation of hot by product is inherent to this process and the Grinder fleet are all already heavily guarded to prevent sparks igniting lineside vegetation and assets | Network Rail procedure adhered to and improved as part of overall climate change and sustainability programmes Plant Asset Manager keeps fire suppression system fit for purpose | Risk to transport from high and low temperatures, high winds, lightning
PLT57 | Asset | On-track machines - renewals | Overhead Condition Renewal Fleet | High winds | Direct | Mobile Elevated Mobile Platforms(MEWPs) and cranes can not work in excessive wind conditions - MEWPs windspeed exceeding 28mph (12.5m/s) - Manbaskets windspeed exceeding 25mph (11.5m/s) - Mobile Cranes normally 31mph (13.5m/s) | Whole country | Professional Head of Plant & Asset Manager | Wind speed | Hazard is specifically covered for MEWPs in BS EN 280: 2013+A1:2015 (Mobile Elevated working platforms, design calculations. stability criteria. construction. safety. examinations and tests). 28mph (12.5m/s) - BS 7121(Code of practice for safe use of cranes) Manbaskets windspeed exceeding 25mph (11.5m/s) - Mobile Cranes normally 31mph (13.5m/s) - Duty charts should specify from each manufacturer | 1/minor | Medium | There is an existing stablished process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure OTMs are less susceptible to effects of wind because they are normally permanently coupled with another vehicle in working mode. This is unlike Mobile or On-Track Plant MEWPs which normally alone | 1/minor | 1/minor | Medium | There is an existing stablished process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure. NR/GN/ESD23 Issue 1,'Climate Change Projections' Section 11 -Wind. Conclusion: - Global projections over the UK shows increases in near surface wind speeds in the 2nd half of the 21st Century, - For the winter season, when more significant impacts of wind are experience this is accompanied by an increase in frequency of winter storms over the UK, and - That the increase in wind speeds is modest compared to interannual variability | Network Rail procedure adhered to and improved as part of overall climate change and sustainability programmes Modest wind speed increase does not required increase in current working wind speed limit unless specifically requested by NR frontline of Principal Contractors | Risk to transport from high and low temperatures, high winds, lightning
PLT58 | Asset | On-track machines - renewals | HOPS | High winds | Direct | Mobile Elevated Mobile Platforms(MEWPs) and cranes can not work in excessive wind conditions - MEWPs windspeed exceeding 28mph (12.5m/s) - Manbaskets windspeed exceeding 25mph (11.5m/s) - Mobile Cranes normally 31mph (13.5m/s) | Whole country | Professional Head of Plant & Asset Manager | Wind speed | Hazard is specifically covered for MEWPs in BS EN 280: 2013+A1:2015 (Mobile Elevated working platforms, design calculations. stability criteria. construction. safety. examinations and tests). 28mph (12.5m/s) - BS 7121(Code of practice for safe use of cranes) Manbaskets windspeed exceeding 25mph (11.5m/s) - Mobile Cranes normally 31mph (13.5m/s) - Duty charts should specify from each manufacturer | 1/minor | Medium | There is an existing stablished process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure OTMs are less susceptible to effects of wind because they are normally permanently coupled with another vehicle in working mode. This is unlike Mobile or On-Track Plant MEWPs which normally alone | 1/minor | 1/minor | Medium | There is an existing stablished process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure. NR/GN/ESD23 Issue 1,'Climate Change Projections' Section 11 -Wind. Conclusion: - Global projections over the UK shows increases in near surface wind speeds in the 2nd half of the 21st Century, - For the winter season, when more significant impacts of wind are experience this is accompanied by an increase in frequency of winter storms over the UK, and - That the increase in wind speeds is modest compared to interannual variability | Network Rail procedure adhered to and improved as part of overall climate change and sustainability programmes Modest wind speed increase does not required increase in current working wind speed limit unless specifically requested by NR frontline of Principal Contractors | Risks to subterranean and surface infrastructure from subsidence
PLT59 | Asset | On-track machines - seasonal & incident | Breakdown cranes | High winds | Direct | Mobile Elevated Mobile Platforms(MEWPs) and cranes can not work in excessive wind conditions - MEWPs windspeed exceeding 28mph (12.5m/s) - Manbaskets windspeed exceeding 25mph (11.5m/s) - Mobile Cranes normally 31mph (13.5m/s) | Whole country | Professional Head of Plant & Asset Manager | Wind speed | Hazard is specifically covered for MEWPs in BS EN 280: 2013+A1:2015 (Mobile Elevated working platforms, design calculations. stability criteria. construction. safety. examinations and tests). 28mph (12.5m/s) - BS 7121(Code of practice for safe use of cranes) Manbaskets windspeed exceeding 25mph (11.5m/s) - Mobile Cranes normally 31mph (13.5m/s) - Duty charts should specify from each manufacturer | 1/minor | Medium | There is an existing stablished process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure OTMs are less susceptible to effects of wind because they are normally permanently coupled with another vehicle in working mode. This is unlike Mobile or On-Track Plant MEWPs which normally alone | 1/minor | 1/minor | Medium | There is an existing stablished process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure. NR/GN/ESD23 Issue 1,'Climate Change Projections' Section 11 -Wind. Conclusion: - Global projections over the UK shows increases in near surface wind speeds in the 2nd half of the 21st Century, - For the winter season, when more significant impacts of wind are experience this is accompanied by an increase in frequency of winter storms over the UK, and - That the increase in wind speeds is modest compared to interannual variability | Network Rail procedure adhered to and improved as part of overall climate change and sustainability programmes Modest wind speed increase does not required increase in current working wind speed limit unless specifically requested by NR frontline of Principal Contractors | Risk to transport from high and low temperatures, high winds, lightning
PLT60 | Asset | On-track machines - seasonal & incident | Snow fleet | Snow | Direct | Snow fall rate above working limit of machine | Whole country | Professional Head of Plant & Asset Manager | Predicted Snow fall rate | Snow Fleet have a minimum and maximum working limit. Risk is operational | 2/minor | Medium | There is an established process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure | 2/minor | 2/minor | Medium | There is an established process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure. Climate Change Projection Guidance, Section 6.3 Snow. 'The conclusions of the study were the following quantitative narratives: - A reduction in the mean number of winter snow fall days by the 2080s of between -55% in western Scotland to -85% in the south of England - A reduction in heavy snow fall events of -60% in Scotland and more than -80% for the rest of the UK | Network Rail Shift planning process includes consideration of extreme weather condition. Therefore plant is likely to be working because fleet will be strategically distributed and tactically operated during times of heavy snowfall | Risk to transport from high and low temperatures, high winds, lightning
PLT61 | Asset | On-track machines - seasonal & incident | Snow & ice treatment train | Snow/ice | Indirect | Snow & Ice volume above threshold machine is designed to clear | Whole country | Professional Head of Plant & Asset Manager | Predicted Snow fall rate and ice formation | Snow Fleet have a minimum and maximum working limit. Risk is operational | 2/minor | Medium | There is an established process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure | 2/minor | 2/minor | Medium | There is an established process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure. Climate Change Projection Guidance, Section 6.3 Snow. 'The conclusions of the study were the following quantitative narratives: - A reduction in the mean number of winter snow fall days by the 2080s of between -55% in western Scotland to -85% in the south of England - A reduction in heavy snow fall events of -60% in Scotland and more than -80% for the rest of the UK | Network Rail Shift planning process includes consideration of extreme weather condition. Therefore plant is likely to be working because fleet will be strategically distributed and tactically operated during times of heavy snowfall | Risk to transport from high and low temperatures, high winds, lightning
PLT62 | Asset | Portable transportable plant | Generators, powered hand tools, lighting rigs, track jacks | Extreme hot days | Direct | Machine engine overheats leading to machine fire risk | Whole country | Professional Head of Plant & Asset Manager | Engine overheat limit specific to engine type; fire prevention requirements set in standard | - Hazard is specifically mentioned in clause 1.5.6 Fire of Machinery Directive 2006/42/EC - Hazard is not covered in RIS-1701-PLT Issue 2 - Rail Industry Standard for the Design of On-Track Machines in Travelling and Working Mode - Hazard is not covered in BS EN 13977:2011 - Railway applications. Track. Safety requirements for portable machines and trolleys for construction and maintenance | 1/minor | Medium | Hazard is specifically covered in legislation only | 1/minor | 1/minor | Medium | Hazard is specifically covered in legislation only | Machine Operator stores plant equipment correctly and refuels engine driven equipment correctly | Risk to transport from high and low temperatures, high winds, lightning
PLT63 | Asset | Portable transportable plant | Generators, powered hand tools, lighting rigs, track jacks | Higher average temperature | Direct | Lineside PTP suffer overheat and breakdown quicker than designed - thermal fatigue | Whole country | Professional Head of Plant & Asset Manager | None | Decision threshold criteria does not apply, these factors are already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes. In addition these machines are not made only for the UK but also for countries with higher temperature such as Italy, North America and North Africa | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | 1/minor | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables. (2) Plant Supplier hires machine that is fit for purpose and reflects increased cost in hire rate (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT64 | Asset | Portable transportable plant | Generators, powered hand tools, lighting rigs, track jacks | Heat wave | Direct | Lineside PTP suffer overheat and breakdown quicker than designed - thermal fatigue | Whole country | Professional Head of Plant & Asset Manager | None | Decision threshold criteria does not apply, these factors are already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes. In addition these machines are not made only for the UK but also for countries with higher temperature such as Italy, North America and North Africa | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | 1/minor | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables. (2) Plant Supplier hires machine that is fit for purpose and reflects increased cost in hire rate (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT65 | Asset | Portable transportable plant | Generators, powered hand tools, lighting rigs, track jacks | Long hot, dry summer | Direct | Lineside PTP suffer overheat and breakdown quicker than designed - thermal fatigue | Whole country | Professional Head of Plant & Asset Manager | None | Decision threshold criteria does not apply, these factors are already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes. In addition these machines are not made only for the UK but also for countries with higher temperature such as Italy, North America and North Africa | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | 1/minor | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables. (2) Plant Supplier hires machine that is fit for purpose and reflects increased cost in hire rate (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT66 | Asset | Portable transportable plant | Generators, powered hand tools, lighting rigs, track jacks | Large diurnal temperature range | Direct | Lineside PTP suffer overheat and breakdown quicker than designed - thermal fatigue | Whole country | Professional Head of Plant & Asset Manager | None | Decision threshold criteria does not apply, these factors are already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes. In addition these machines are not made only for the UK but also for countries with higher temperature such as Italy, North America and North Africa | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | 1/minor | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables. (2) Plant Supplier hires machine that is fit for purpose and reflects increased cost in hire rate (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT67 | Asset | Depot plant | Anti-freeze systems, carriage washing machines, cranes, fuelling system, jacks, turntables, bogie/wheel drop, underframe cleaning system, depot protection, interceptors, shore supplies, wheel lathe and shunter | Extreme hot days | Direct | Thermal stressing leading to shorter component lifespan and higher consumables (oil, water, wiring) | Whole country | Professional Head of Plant & Asset Manager | None | Decision threshold criteria does not apply, these factors are already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes. In addition these machines are not made only for the UK but also for countries with higher temperature such as Italy, North America and North Africa | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | 1/minor | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables. (2) Plant Supplier hires machine that is fit for purpose and reflects increased cost in hire rate (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT68 | Asset | Depot plant | Anti-freeze systems, carriage washing machines, cranes, fuelling system, jacks, turntables, bogie/wheel drop, underframe cleaning system, depot protection, interceptors, shore supplies, wheel lathe and shunter | Heat wave | Direct | Thermal stressing leading to shorter component lifespan and higher consumables (oil, water, wiring) | Whole country | Professional Head of Plant & Asset Manager | None | Decision threshold criteria does not apply, these factors are already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes. In addition these machines are not made only for the UK but also for countries with higher temperature such as Italy, North America and North Africa | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | 1/minor | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables (2) Plant Supplier hires machine that is fit for purpose and reflects increased cost in hire rate (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT69 | Asset | Depot plant | Anti-freeze systems, carriage washing machines, cranes, fuelling system, jacks, turntables, bogie/wheel drop, underframe cleaning system, depot protection, interceptors, shore supplies, wheel lathe and shunter | Higher average temperature | Direct | Thermal stressing leading to shorter component lifespan and higher consumables (oil, water, wiring) | Whole country | Professional Head of Plant & Asset Manager | None | Decision threshold criteria does not apply, these factors are already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes. In addition these machines are not made only for the UK but also for countries with higher temperature such as Italy, North America and North Africa | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | 1/minor | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables (2) Plant Supplier hires machine that is fit for purpose and reflects increased cost in hire rate (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT70 | Asset | Depot plant | Anti-freeze systems, carriage washing machines, cranes, fuelling system, jacks, turntables, bogie/wheel drop, underframe cleaning system, depot protection, interceptors, shore supplies, wheel lathe and shunter | Large diurnal temperature range | Direct | Thermal stressing leading to shorter component lifespan and higher consumables (oil, water, wiring) | Whole country | Professional Head of Plant & Asset Manager | None | Decision threshold criteria does not apply, these factors are already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes. In addition these machines are not made only for the UK but also for countries with higher temperature such as Italy, North America and North Africa | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | 1/minor | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables (2) Plant Supplier hires machine that is fit for purpose and reflects increased cost in hire rate (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT71 | Asset | Depot plant | Anti-freeze systems | Snow/ice | Direct | Temperature drop seizes weakest link within the system e.g. control module | Whole country | Professional Head of Plant & Asset Manager | Weather Warning | Hazard is not specifically mentioned in Machinery Directive 2006/42/EC | 2/Minor | Medium | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address hazard | 2/minor | 2/minor | Medium | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address hazard | Operational parameters enables effective operation and would therefore would be able to cope with future reduced snowfall and ice build-up | Risk to transport from high and low temperatures, high winds, lightning
PLT72 | Asset | Depot plant | Carriage washing machines | Snow/ice | Direct | Temperature drop seizes weakest link within the system e.g. control module | Whole country | Professional Head of Plant & Asset Manager | Min -20 Deg C | Hazard is not specifically mentioned in Machinery Directive 2006/42/EC Hazard is specifically covered in Section 4.7 Water Storage and supply of NR/L2/RVE/0130, Design and Installation of Carriage Washing Machines | 1/Minor | Medium | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address hazard | 1/minor | 1/minor | Medium | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address hazard | That plant suppliers will provide machines that address the hazard That incidences of snow/ice are projected to reduce | Risk to transport from high and low temperatures, high winds, lightning
PLT73 | Asset | Depot plant | Carriage washing machines | Lightning | Direct | Short circuiting of electro-mechanical control module | Whole country | Professional Head of Plant & Asset Manager | Weather Warning | - Hazard is specifically mentioned in clause 1.5.16 Lightning of Machinery Directive 2006/42/EC | 2/minor | Medium | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address lightning | 2/minor | 2/minor | Medium | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address lightning Means of making plant lighting proof to be investigated - Action 2 UKCP09 technical note - Future changes in lightening from the UKCP09 ensemble of regional climate model projections. Section 9 Summary...'increases in the number of lightening days are projected for all four seasons across the whole of the UK' | Carriage Washer adequately earthed | Risk to transport from high and low temperatures, high winds, lightning
PLT74 | Asset | Depot plant | Underframe cleaning system, shore supplies; wheel lathes and shunters | Flooding | Interdependency (them on us) | Unable to use plant due to inability to access submerged plant | Whole country | Professional Head of Plant & Asset Manager | Weather Warning | Building integrity compromised | 2/minor | Medium | There is an established process for avoiding this scenario also used for shift planning. Increase chance of implementation because of broader coverage of procedure | 4/moderate | 4/moderate | Medium | There is an established process for avoiding this scenario, also the pre-check process would be able to determine if the system in question is still fit for purpose. Action 4 NR/GN/ESD23 Issue 1, 'Climate Change Projections Guidance' Section 7 - Flooding…. 'Climate change will significantly increase future flood risk.' | That current process is able to cope with the projected changes in rainfall | Risks to infrastructure services from river, surface water and groundwater flooding
PLT75 | Asset | Depot plant | Gas storage | Lightning | Direct | Short circuiting of electro-mechanical control module | Whole country | Professional Head of Plant & Asset Manager | Weather Warning | - Hazard is specifically mentioned in clause 1.5.16 Lightning of Machinery Directive 2006/42/EC | 3/minor | Low | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address lightning | 3/minor | 3/minor | Low | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address lightning Means of making plant lighting proof to be investigated - Action 2 UKCP09 technical note - Future changes in lightening from the UKCP09 ensemble of regional climate model projections. Section 9 Summary...'increases in the number of lightening days are projected for all four seasons across the whole of the UK' | Gas storage installed in facility which is lighting proof | Risk to transport from high and low temperatures, high winds, lightning
PLT76 | Asset | Fixed plant | Moving bridges | Lightning | Direct | Short circuiting of electro-mechanical control module | Whole country | Professional Head of Plant & Asset Manager | Weather Warning | Hazard is specifically mentioned in clause 1.5.16 Lightning of Machinery Directive 2006/42/EC | 3/minor | Low | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address lightning | 3/minor | 3/minor | Low | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address lightning Means of making plant lighting proof to be investigated - Action 2 UKCP09 technical note - Future changes in lightening from the UKCP09 ensemble of regional climate model projections. Section 9 Summary...'increases in the number of lightening days are projected for all four seasons across the whole of the UK' | Gas storage installed in facility which is lighting proof | Risk to transport from high and low temperatures, high winds, lightning
PLT77 | Asset | Fixed plant | Gas point Heaters, hydraulic buffers, moving bridge | Snow/ice | Direct | Temperature drop seizes weakest link within the system e.g. control module | Whole country | Professional Head of Plant & Asset Manager | Weather Warning | Hazard is not specifically mentioned in Machinery Directive 2006/42/EC | 3/minor | Low | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address hazard | 3/minor | 3/minor | Medium | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address hazard | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables. (2) Project Manager and Project Engineer procure machine that is fit for purpose (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT78 | Asset | Fixed plant | Gas point Heaters, hydraulic buffers, moving bridge | Snow/ice | Direct | Temperature drop seizes weakest link within the system e.g. control module | Whole country | Professional Head of Plant & Asset Manager | Weather Warning | Hazard is not specifically mentioned in Machinery Directive 2006/42/EC | 3/minor | Low | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address hazard | 3/minor | 3/minor | Medium | Reliance on plant converter/manufacturer and supplier to have devised an engineering means to address hazard | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables. (2) Project Manager and Project Engineer procure machine that is fit for purpose (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT79 | Asset | Fixed plant | Gas point heaters, gas storage, pumps, hydraulic buffers, tunnel ventilation fans, moving bridge | Extreme hot days | Direct | Thermal stressing leading to shorter component lifespan and higher consumables (oil, water, wiring) | Whole country | Professional Head of Plant & Buildings/ Structural Asset Manager | Weather Warning | Decision threshold criteria does not apply, these factors are already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes. In addition these machines are not made only for the UK but also for countries with higher temperature such as Italy, North America and North Africa | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | 1/minor | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables (2) Project Manager and Project Engineer procure machine that is fit for purpose (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT80 | Asset | Fixed plant | Gas point heaters, gas storage, pumps, hydraulic buffers, tunnel ventilation fans, moving bridge | Heat wave | Direct | Thermal stressing leading to shorter component lifespan and higher consumables (oil, water, wiring) | Whole country | Professional Head of Plant & Buildings/ Structural Asset Manager | Weather Warning | Decision threshold criteria does not apply, these factors are already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes. In addition these machines are not made only for the UK but also for countries with higher temperature such as Italy, North America and North Africa | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | 1/minor | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables. (2) Project Manager and Project Engineer procure machine that is fit for purpose (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT81 | Asset | Fixed plant | Gas point heaters, gas storage, pumps, hydraulic buffers, tunnel ventilation fans, moving bridge | Higher average temperature | Direct | Thermal stressing leading to shorter component lifespan and higher consumables (oil, water, wiring) | Whole country | Professional Head of Plant & Buildings/ Structural Asset Manager | Weather Warning | Decision threshold criteria does not apply, these factors are already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes. In addition these machines are not made only for the UK but also for countries with higher temperature such as Italy, North America and North Africa | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | 1/minor | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables. (2) Project Manager and Project Engineer procure machine that is fit for purpose (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
PLT82 | Asset | Fixed plant | Gas point heaters, gas storage, pumps, hydraulic buffers, tunnel ventilation fans, moving bridge | Large diurnal temperature range | Direct | Thermal stressing leading to shorter component lifespan and higher consumables (oil, water, wiring) | Whole country | Professional Head of Plant & Buildings/ Structural Asset Manager | Weather Warning | Decision threshold criteria does not apply, these factors are already considered as part of the design, A larger range will simply shorten plant asset lifespan and require more frequent replacement unless asset management strategy changes. In addition these machines are not made only for the UK but also for countries with higher temperature such as Italy, North America and North Africa | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | 1/minor | 1/minor | Medium | Operational & storage thermal duty cycle already forms part of specification writing process | (1) Plant Asset Manager monitors component failure trends and increase in volume of consumables. (2) Project Manager and Project Engineer procure machine that is fit for purpose (3) Plant Asset Manager and Supplier has set up availability, reliability and early warning indicator KPIs | Risk to transport from high and low temperatures, high winds, lightning
SIG1 | Asset | Signalling | Interlocking | Extreme hot days | Direct | SSI and peripheral equipment overheat | Whole country | Professional Head of Signalling | Life expired interlocking or component failure | Equipment located in passive loc cases at risk of overheating, particularly where sun hats are not used and orientation gives the worst solar gain | 6/moderate | Medium | Historic evidence has shown SSI and PSU failures are higher during hot days | 6/moderate | N/A | Medium | Nationally not a big issue in 2050 as the number of SEUs will have dropped from 65000 to 6000 Areas still with SSI in 2050 should expect a higher frequency of SSI failures on hot days. In 2080 - this equipment will have been removed | Assuming NR follow the current long term deployment plan | Risk to transport from high and low temperatures, high winds, lightning
SIG10 | Asset | Signalling | Signals | Lightning | Direct | Electromagnetic event on electrical equipment leading to failure | Whole country | Professional Head of Signalling | Life expired or product failure | Signals should fail right side however LED signals are more susceptible to failure wrong side if hit by lightning | 2/minor | Medium | Random failure and somewhat infrequent. LED signals more prone to failure Previous signal and route knowledge mitigate against a major event. If a signal is put back to danger (out of sequence signal) then there is potential for a major event however extremely unlikely (incredible) | 4/moderate | N/A | Medium | As the long term deployment plan roles out there will be a reduction in the signal population reducing the risk of failure however the frequency of storms will increase. The risk for remaining signals will increase until all signals are removed | Assuming NR follow the current long term deployment plan. IP rating of product is specified to meet IP67 (submerged) so not envisaged to be a big problem. This is assuming our SICA assessments pick up any degrading/degraded ground mounted units | Risk to transport from high and low temperatures, high winds, lightning
SIG11 | Asset | Signalling | Signals | High winds | Direct | Old signal posts blowing over, aging structural connections potential for breaking | Whole country | Professional Head of Signalling | Life expired or product failure | As the population ages the frequency of signal post failure increases | 6/moderate | Medium | Aging signal posts are difficult to assess and predict how much life remains. Potential WSF exists if the signal falls over maintaining its proving (Driver misses a yellow and arrives at a red at line speed) | 6/moderate | N/A | Medium | SICA assessment will continue however approximately 10% of assets are checked during a SICA assessment. This combined with a vastly reduce signal post population and increase in wind will not increase our risk. A little reality - People are likely to try and extend the life of signal posts as their days are numbered, this could lead to a higher risk as they have a finite life with an often hidden failure mode 2080: No conventional signalling | Assuming NR follow the current long term deployment plan | Risk to transport from high and low temperatures, high winds, lightning
SIG12 | Asset | Signalling | Location case | Large diurnal temperature range | Direct | Condensation forms inside loc case on coldest materials leading to a short circuit/premature failure | Whole country | Professional Head of Signalling | Life expired or product failure | This phenomena is generally seen around Spring and Autumn | 4/moderate | Medium | Some equipment housed within location case are not protected against dripping water. This is a bigger problem for enclosures with little heat dissipation inside | 6/moderate | 6/moderate | Medium | This is an issue we see today however it does not always cause an immediate problem. The risk is mitigated slightly as we will have a reduction in location case population by 2050 and 2080 however the equipment we intend to place inside them is likely to be more advanced requiring a fit for purpose environment The Signalling product Acceptance team are more aware of this requirement today than ever before | Assuming NR follow the current long term deployment plan The environmental knowledge is not lost from the product acceptance teams | Risk to transport from high and low temperatures, high winds, lightning
SIG13 | Asset | Signalling | Location case | Low soil moisture | Direct | Impedance to earth could increase leading to more EMC issues for equipment | Whole country | Professional Head of Signalling | Life expired or product failure | Equipment that was previously resilient may start to cause problems | 4/moderate | Medium | Dry soil = higher impedance resulting in less transients being dissipated to earth | 6/moderate | 6/moderate | Medium | This will also be a problem today however it goes largely unnoticed. This could become more of an issue with an increase in local EMI | Local sources of EMI will not dramatically increase | Risk to transport from high and low temperatures, high winds, lightning
SIG14 | Asset | Signalling | Location case | Extreme hot days | Direct | Components housed within the location case can overheat | Whole country | Professional Head of Signalling | Life expired or product failure | Equipment designed to BR 967 was designed for a maximum ambient of 60DegC. More modern equipment is designed to 70DegC. We have datalogger information showing temperatures up to 75DegC already on particularly hot days | 9/moderate | High | This could be our biggest problem and something we already suffer significant delay minutes from | 12/major | 12/major | High | Equipment in use today does not always contain enough margin to give a satisfactory performance on hot days | Location cases do not have any form of active/passive cooling | Risk to transport from high and low temperatures, high winds, lightning
SIG15 | Asset | Signalling | Location case | Heat wave | Direct | Components housed within the location case can overheat | Whole country | Professional Head of Signalling | Life expired or product failure | Equipment designed to BR 967 was designed for a maximum ambient of 60DegC. More modern equipment is designed to 70DegC. We have datalogger information showing temperatures up to 75DegC already on particularly hot days | 9/moderate | High | Equipment in use today is often being used at its limit on hot days | 12/major | 12/major | High | Equipment in use today does not always contain enough margin to give a satisfactory performance on hot days | Location cases do not have any form of active/passive cooling | Risk to transport from high and low temperatures, high winds, lightning
SIG16 | Asset | Signalling | Lineside signalling cable | Erosion | Direct | Stretched/ broken lineside cable after landslide | Whole country | Professional Head of Signalling | Life expired or product failure | Ground movement often stretches cable leading to potential breakages | 6/moderate | Medium | Trains may not be running due to a track defect rather than signalling fault. Also not all landslides lead to a signalling cabling issue | 6/moderate | 9/moderate | Medium | As more rain water falls we are likely to see an increase in the number and severity of landslides. | Assuming this is not made worse by local building/water runoff | Risks to infrastructure services from river, surface water and groundwater flooding
SIG17 | Asset | Signalling | Lineside signalling cable | Flooding | Direct | Reduced core to core and core to earth impedance | Whole country | Professional Head of Signalling | Life expired or product failure | degraded cables can let in water leading to low impedance between cores and earth | 6/moderate | Medium | Generally not a problem with new cable however rodent impact cable or UV effected cable can give a problem | 9/moderate | 9/moderate | Medium | This is an ongoing problem and nothing new, we struggle to combat rodents and have suffered from the effects of UV in the past | Assuming NR follow the current long term deployment plan we will have less cabling for rodents to attack | Risks to infrastructure services from river, surface water and groundwater flooding
SIG18 | Asset | Signalling | AWS | Flooding | Direct | Submerging of AWS magnets may led to failure (incorrect or no indication given to driver). Water ingress into four foot equipment and associated lineside disconnection boxes | Whole country | Professional Head of Signalling | Local flooding of the track will prompt a limit of train movements (either a speed restriction or line closed) | This will be most prevalent in low lying areas, coastal areas or areas with poor drainage | 3/minor | Medium | Saturation of cabling and components requires testing after flooding, replacement depends on damage and results of test | 6/moderate | N/A | Low | If localised flooding becomes more frequent this may affect operation of AWS equipment, especially if equipment is repeatedly submerged or submerged for long periods of time | Risk scores and narrative based on 'no additional adaption' - long term plan is to replace AWS with ETCS ETCS fitment will reduce number of TCs significantly in 2050 and completely by 2080 | Risks to infrastructure services from river, surface water and groundwater flooding
SIG19 | Asset | Signalling | TPWS | Extreme hot days | Direct | Failure of electronic equipment due to high temperatures | Whole country | Professional Head of Signalling | Speed restrictions are enforced during high temperatures | On extreme hot days speed reductions limits the risk caused by a failed TPWS system | 6/moderate | Medium | Historic information shows TPWS is affected by high temperatures | 6/moderate | N/A | Low | Increased temperatures will increase failure rates of TPWS equipment | Risk scores and narrative based on 'no additional adaption' - long term plan is to replace AWS with ETCS ETCS fitment will reduce number of TCs significantly in 2050 and completely by 2080 | Risk to transport from high and low temperatures, high winds, lightning
SIG2 | Asset | Signalling | Interlocking | Heat wave | Direct | SSI and peripheral equipment overheat | Whole country | Professional Head of Signalling | Life expired interlocking or component failure | Equipment located in passive loc cases at risk of overheating, particularly where sun hats are not used and orientation gives the worst solar gain | 6/moderate | Medium | Historic evidence has shown SSI and PSU failures are higher during hot days | 6/moderate | N/A | Medium | Nationally not a big issue in 2050 as the number of SEUs will have dropped from 65000 to 6000 Areas still with SSI in 2050 should expect a higher frequency of SSI failures on hot days. In 2080 - this equipment will have been removed | Assuming NR follow the current long term deployment plan | Risk to transport from high and low temperatures, high winds, lightning
SIG20 | Asset | Signalling | TPWS | Flooding | Direct | Submerging of TPWS equipment may lead to failure (no emergency brake application when required or spurious brake application when not required). Water ingress into four foot equipment and associated lineside disconnection boxes | Whole country | Professional Head of Signalling | Local flooding of the track will prompt a limit of train movements (either a speed restriction or line closed) | This will be most prevalent in low lying areas, coastal areas or areas with poor drainage | 6/moderate | Medium | Saturation of cabling and components requires testing after flooding, replacement depends on damage and results of test. Speed reduction limits the risk caused by a failed TPWS system | 6/moderate | N/A | Low | If localised flooding becomes more frequent this may affect operation of TPWS equipment, especially if equipment is repeatedly submerged or submerged for long periods of time | Risk scores and narrative based on 'no additional adaption' - long term plan is to replace AWS with ETCS ETCS fitment will reduce number of TCs significantly in 2050 and completely by 2080 | Risks to infrastructure services from river, surface water and groundwater flooding
SIG21 | Asset | Signalling | Track Circuit | Extreme hot days | Indirect | Failure of Insulated Rail Joints due to track expansion causes track circuit failure | Whole country | Professional Head of Signalling | Speed restrictions are enforced during high temperatures Or in some cases the track circuit may fail before the track does. Subsequent repairs could necessitate a speed restriction until it is fixed | Risk across whole country although highest risk in area with the biggest temperature increase | 6/moderate | Medium | This is a known issue | 6/moderate | N/A | Low | Increasing temperature will lead to more track expansion causing further IRJ failure | Risk scores and narrative based on 'no additional adaption' - long term plan is to replace AWS with ETCS ETCS fitment will reduce number of TCs significantly in 2050 and completely by 2080 | Risk to transport from high and low temperatures, high winds, lightning
SIG22 | Asset | Signalling | Track Circuit | Extreme hot days | Direct | Failure of electronic equipment such as receivers, transmitters and tuning units | Whole country | Professional Head of Signalling | Speed restrictions are enforced during high temperatures. This statement is not true as the track circuit could fail before the track | Risk across whole country although highest risk in area with the biggest temperature increase | 6/moderate | Medium | Historic information shows electrical equipment associated from track circuits fails more during periods of hot weather | 6/moderate | N/A | Low | Increasing temperature will lead to further failures | Risk scores and narrative based on 'no additional adaption' - long term plan is to replace AWS with ETCS ETCS fitment will reduce number of TCs significantly in 2050 and completely by 2080 | Risk to transport from high and low temperatures, high winds, lightning
SIG23 | Asset | Signalling | Track circuit | High average rainfall over several days | Direct | Low ballast resistance due to wet weather | Whole country | Professional Head of Signalling | Signaller may observe intermittent right-side failure i.e. Showing Occupied When Clear | Areas prone to wet ballast tend to be known | 6/moderate | Medium | Historic information shows wet ballast is any issue for track circuits | 6/moderate | N/A | Low | Wetter conditions will increase the occurrence of the risk | Long term plan to replace track circuits with axle counters or train based location systems ETCS fitment will reduce number of TCs significantly in 2050 and completely by 2080 | Risks to infrastructure services from river, surface water and groundwater flooding
SIG24 | Asset | Signalling | Track circuit | Flooding | Direct | Saturation of IRJs, flooding of disconnection boxes and tail cable water ingress may all result in failure of the track circuit | Whole country | Professional Head of Signalling | Signaller may observe intermittent SOWC | This will be most prevalent in low lying areas, coastal areas or areas with poor or no drainage | 6/moderate | Medium | Saturation of cabling and components requires testing after flooding, replacement depends on damage and results of test | 6/moderate | N/A | Low | Wetter conditions will increase the occurrence of the risk | Long term plan to replace track circuits with axle counters or train based location systems ETCS fitment will reduce number of TCs significantly in 2050 and completely by 2080 | Risks to infrastructure services from river, surface water and groundwater flooding
SIG25 | Asset | Signalling | Track circuit | Flooding | Direct | Submerging of impedance bonds | Whole country | Professional Head of Signalling | Local flooding of the track will prompt a limit of train movements (either a speed restriction or line closed) | This will be most prevalent in low lying areas, coastal areas or areas with poor or no drainage | 6/moderate | Medium | Saturation of cabling and components requires testing after flooding, replacement depends on damage and results of test. Impedance bonds are labour intensive to replace. If the track is flooded this will affect the operation of the track circuit anyway but it may take longer to recover | 6/moderate | N/A | Low | If localised flooding becomes more frequent this may affect operation of track circuit equipment, especially if equipment is repeatedly submerged or submerged for long periods of time | Long term plan to replace track circuits with axle counters or train based location systems ETCS fitment will reduce number of TCs significantly in 2050 and completely by 2080 | Risks to infrastructure services from river, surface water and groundwater flooding
SIG26 | Asset | Signalling | Track circuit | Storms | Indirect | Leaf fall | Whole country | Professional Head of Signalling | Leaf fall can provide an insulating layer between wheel and rail causing the track circuit to SCWO | Unable to map to climate variable. Leaf fall induced adhesion is a combination of weather events. The nearest category is storms as it includes rain, wind, however this only applies in Autumn | 12/major | Medium | A well known problem with leaf fall caused by the combined effects of wind and rain | 9/moderate | N/A | Low | It's not known how climate change will effect leaf fall. The projections give no specific guidance although it can be anticipated that there will be some change. Whether the change is better or worse than the current situation is unknown | Assumed no change to current risk as effect of climate change on leaf fall is currently unknown ETCS fitment will reduce number of TCs significantly in 2050 and completely by 2080 | Risks to infrastructure services from river, surface water and groundwater flooding | Risk to transport from high and low temperatures, high winds, lightning
SIG27 | Asset | Signalling | Axle counter/treadle | Flooding | Direct | Submerging of axle counter/treadle heads | Whole country | Professional Head of Signalling | Local flooding of the track will prompt a limit of train movements (either a speed restriction or line closed) | This will be most prevalent in low lying areas, coastal areas or areas with poor drainage | 6/moderate | Medium | Saturation of cabling and components requires testing after flooding, replacement depends on damage and results of test | 8/moderate | 12/major | Low | If localised flooding becomes more frequent this may affect operation of axle counter/treadle equipment, especially if equipment is repeatedly submerged or submerged for long periods of time | Aging of product does not disproportionately impact upon housing IP rating | Risks to infrastructure services from river, surface water and groundwater flooding
SIG28 | Asset | Signalling | Axle counter/treadle | Extreme hot days | Direct | Failure of electronic equipment such as evaluators and cards | Whole country | Professional Head of Signalling | Speed restrictions are enforced during high temperatures. This statement is not strictly true as the axle counter could fail before the track | Risk across whole country although highest risk in area with the biggest temperature increase | 6/moderate | Medium | Historic information shows link between high temperatures and failure of axle counter/treadle equipment | 8/moderate | 12/major | Low | Increasing temperature will lead to further failures | Aging of product does not disproportionately impact upon housing IP rating | Risk to transport from high and low temperatures, high winds, lightning
SIG29 | Asset | Signalling | Axle counter | Flooding | Direct | Submerging of EAK units will cause water ingress into sensitive electronic equipment | Whole country | Professional Head of Signalling | Local flooding of the track will prompt a limit of train movements (either a speed restriction or line closed) | This will be most prevalent in low lying areas, coastal areas or areas with poor drainage | 6/moderate | Medium | Saturation of cabling and components requires testing after flooding, replacement depends on damage and results of test. Sensitive electronic equipment is likely to be damaged by water ingress and require replacement | 8/moderate | 12/major | Low | If localised flooding becomes more frequent this may affect operation of axle counter/treadle equipment, especially if equipment is repeatedly submerged or submerged for long periods of time | Aging of product does not disproportionately impact upon housing IP rating | Risks to infrastructure services from river, surface water and groundwater flooding
SIG3 | Asset | Signalling | Interlocking | Flooding | Direct | Flooding of loc case | Whole country | Professional Head of Signalling | Life expired interlocking or component failure | Equipment housed within location cases and unprotected control rooms as risk | 6/moderate | Medium | Generally areas are known for flooding and loc cases are elevated or moved elsewhere | 9/moderate | 9/moderate | Medium | Although in 2050 we will not require the same amount of location cases due to a reduction in lineside signalling we will still have location cases for S&C and ETCS LEU equipment. 2080: a further reduction in Location cases will be seen however the likelihood will again increase A proactive campaign would dramatically reduce the likelihood of this event | Assuming we are unresponsive to the rising threat of flooding we are likely to see an increased risk due to an increase in frequency and severity of storms and rain | Risks to infrastructure services from river, surface water and groundwater flooding
SIG30 | Asset | Signalling | ETCS-trackside | Extreme hot days | Direct | RBC and peripheral equipment overheat | Whole country | Professional Head of Signalling | Life expired sub-systems or component failure | Equipment located in passive lineside equipment housings at risk of overheating, particularly where sun orientation gives the worst solar gain | 6/moderate | Medium | Excluding Cambrian this is relatively new technology. Failure considered likely in the event of failed aircon/cooling during extreme hot weather events | 9/moderate | 9/moderate | Low | This is really about location case management rather than the product itself however the specification of the product should also be a factor | No overlay areas | Risk to transport from high and low temperatures, high winds, lightning
SIG31 | Asset | Signalling | ETCS-trackside | Flooding | Direct | Flooding of 4ft mounted and lineside equipment (LEU, Balises etc) | Whole country | Professional Head of Signalling | Life expired equipment or component failure | Equipment housed within lineside cases and 4ft may be at risk | 6/moderate | Medium | Generally areas are known for flooding and lineside equipment cases are elevated or positioned elsewhere. Excluding Cambrian this is relatively new technology. Failure considered as likely in the event of extreme flood events | 9/moderate | 9/moderate | Low | Some equipment such as our balises and axle counters cannot be moved from the trackside like a location case. Specification of the product is key to its performance | No overlay areas | Risks to infrastructure services from river, surface water and groundwater flooding
SIG32 | Asset | Signalling | ETCS-trackside | Lightning | Direct | RBC and peripheral equipment. Electromagnetic event on electrical equipment | Whole country | Professional Head of Signalling | Life expired equipment or component failure | Equipment located in passive lineside equipment housings at risk. Very difficult and expensive to protect against a direct hit however local lightning strikes can be mitigated | 6/moderate | Medium | Excluding Cambrian this is relatively new technology. Need to consider ETCS trackside sub-systems may be centrally positioned in ROC centres | 6/moderate | 9/moderate | Medium | Equipment designed to modern standards generally have an increased resilience against EMC however direct or very near lightning strikes will inevitability cause issues | No overlay areas | Risk to transport from high and low temperatures, high winds, lightning
SIG4 | Asset | Signalling | Interlocking | Lightning | Direct | Electromagnetic event on electrical equipment | Whole country | Professional Head of Signalling | Life expired interlocking or component failure | Very difficult and expensive to protect against a direct hit however local lightning strikes can be mitigated | 6/moderate | Medium | Lightning is currently infrequent in the UK however when a strike occurs near Signalling equipment we do see failures | 6/moderate | 9/moderate | Medium | As electrical storms increase so will the likelihood of a lightning strike causing a failure. 2050 has not been increased due the removal of conventional SEUs and minor increase in lightning however extremal ETCS equipment will still exists in 2080 when we can expect more frequent storms Equipment with the ability to cause long term significant inconvenience will be located in well protected ROCs | Electrical storms focused over key 'unprotected' areas statistically will increase causing asset failures. Equipment based within ROCs are unlikely to suffer due to the level of protection offered by the building and power supply | Risk to transport from high and low temperatures, high winds, lightning
SIG5 | Asset | Signalling | Signals | Extreme hot days | Direct | Electronics overheating leading to premature failure | Whole country | Professional Head of Signalling | Life expired or product failure | Solar heating combined with an extreme ambient can lead to electronics being pushed beyond their operating parameters | 4/moderate | High | We do not see many signal failures due to heat, normally a weaker component in the chain fails before the signal. Aging LED signals will be more prone to this failure mode | 4/moderate | N/A | High | We do not see a correlation between hot weather and signal head failure however components will be operating without much margin on hot summer days | Assuming NR follow the current long term deployment plan | Risk to transport from high and low temperatures, high winds, lightning
SIG6 | Asset | Signalling | Signals | Snow | Direct | Snow builds up on optics obscuring the aspect increasing SPAD risk | Whole country | Professional Head of Signalling | Life expired or product failure | Greater risk for Northern areas and also LED signals do not heat the lens like a Halogen lamp | 6/moderate | High | Occasionally we get signals covered in snow. This is more of a problem for alphanumeric than CLS | 2/minor | N/A | Medium | Less signals in 2050 along with a reduction in the likelihood of snow will reduce this risk. 2080: No conventional signalling | Assuming NR follow the current long term deployment plan | Risk to transport from high and low temperatures, high winds, lightning
SIG7 | Asset | Signalling | Signals | Light rain/drizzle | Direct | Fog not light rain drizzle - Risk fog obscures signal increase SPAD risk | Whole country | Professional Head of Signalling | Life expired or product failure | Route knowledge will act as a mitigation | 2/minor | Medium | Short term event that the driver should be prepared for. Also the driver has route knowledge mitigating the risk | 2/minor | N/A | Medium | A reduction in likelihood due to less conventional signalling however there will be an increase in storms that could lead to an obscured signal | Assuming NR follow the current long term deployment plan
SIG8 | Asset | Signalling | Signals | Heavy rain/cloudburst | Direct | Rain obscures aspect increasing the SPAD risk | Whole country | Professional Head of Signalling | Life expired or product failure | Route knowledge will act as a mitigation | 2/minor | Medium | Short term event that the driver can prepare for. Also the driver has route knowledge mitigating the risk | 2/minor | N/A | Medium | A reduction in likelihood due to less conventional signalling however there will be an increase in storms that could lead to an obscured signal | Assuming NR follow the current long term deployment plan | Risks to infrastructure services from river, surface water and groundwater flooding | Risk to transport from high and low temperatures, high winds, lightning
SIG9 | Asset | Signalling | Signals | Flooding | Direct | Ground mounted signals potential for ingress of water | Whole country | Professional Head of Signalling | Life expired or product failure | Trains are unlikely to be running if ground mounted signal are covered with water | 4/moderate | Medium | Trains are unlikely to be running if ground mounted signal are submerged | 4/moderate | N/A | Medium | As the long term deployment plan roles out there will be less ground mounted signals reducing the risk. However, there will also be an increase in the frequency and severity of flooding events | Assuming NR follow the current long term deployment plan. The environmental knowledge is not lost from the product acceptance teams | Risks to infrastructure services from river, surface water and groundwater flooding
STR1 | Asset | Structures | Coastal and estuarial protection | Storms | Direct | Adverse and extreme coastal events | Coastal | Professional Head of Structures | Intervention based on Extreme Weather Plans determined by each route | Caused by storm surges, large waves and strong wind, they can elevate sea levels and cause large waves at the coastline. These large waves can overtop coastal defences and cause inundation, erosion, scour, loss of stability and structural damage | 9/moderate | High | Based on past asset failures | 16/major | 20/severe | Medium | Current funding will not ensure resilience of coastal assets against predicted sea level rises | Assume current funding remains for current management practices | Risk to offshore infrastructure from storms and high waves
STR2 | Asset | Structures | Bridges, culverts and retaining walls | Flooding | Direct | Scour | Whole country | Professional Head of Structures | Intervention based on Extreme Weather Plans determined by each route | Bridge scour is the removal of sediment such as sand and gravel from round bridge abutments or piers. Scour, caused by swiftly moving water, can scoop out scour holes, compromising the integrity of a structure | 9/moderate | High | Based on past asset failures | 9/moderate | 12/major | High | NR has robust management processes for current scour risk. Policy is to remediate high risk scour sites. This does not account for climate change, but we are committed to ongoing enhancement of scour assessment techniques | Assume current funding remains for current management practices | Risks to bridges and pipelines from flooding and erosion
STR3 | Asset | Structures | Bridges, culverts and retaining walls | Flooding | Direct | Hydrodynamic loading (including debris impact and buoyancy) | Whole country | Professional Head of Structures | Intervention based on Extreme Weather Plans determined by each route | During a flood, a structure may be partially or entirely submerged by the flow and the subsequent loading of fluid and/or debris can cause structures to collapse. For existing structures, marker plates are installed and monitored during adverse weather events. For newer structures, the risks for uplift are considered in the design. | 9/moderate | High | Based on past asset failures | 12/major | 12/major | Medium | Decks can be strengthened to resist uplift and lateral hydrodynamic forces. Existing structures are monitored and new structures are designed to withstand such forces, but climate change is not currently considered | That current management practices continue, but that Network Rail increase number of buoyancy assessments | Risks to bridges and pipelines from flooding and erosion
STR4 | Asset | Structures | Bridges, culverts and retaining walls. Coastal and estuarial protection | Lightning | Direct | Electrocution | Whole country | Professional Head of Structures | No intervention threshold currently | There is currently no management system. One needs to be developed and either implemented by Professional Head of Structures or ownership by another Asset Function (e.g. E&P) must be agreed | 6/moderate | Medium | The current risk is not significant with electrical insulation provided by other asset disciplines (Signalling and Electrification) to protect assets. No specific control however included in requirements for building/structures design documents. Risk for structures is low, but higher for other disciplines | 6/moderate | 8/moderate | Medium | There is currently no management system for structures, other than bonding protection by other asset disciplines. The although lightning could increase the current protection and maintenance procedures for other disciplines is not expected to worsen | The risk from metal structures is currently unmanaged within Structures discipline and may become worse under climate change projections | Risk to transport from high and low temperatures, high winds, lightning
STR5 | Asset | Structures | Bridges, culverts and retaining walls | Snow/ice | Direct | Deterioration of condition of asset | Whole country | Professional Head of Structures | Mainly through icicle formation in tunnels and weathering of material | On icicles, there is an established process of managing tunnel shafts and therefore risks are minimal. The rate of weathering is a function of exposure and material constituting the asset. This mainly impacts structures with concrete encasement of structures with soft bricks. The risks are managed as BAU through tapping surveys. There is no special requirement within policy to manage structures until such time they are rendered unserviceable. Bridges are most critical and routine structural assessments gauge the impact of weathering on the capability of assets. No further policy intervention is required | 9/moderate | High | Based on past assets failures | 9/moderate | 6/moderate | High | There are established risk based approaches used to determine which structures may require further intervention. At this stage this is managed by removing dislodged material. Risk reduction in 2080 is assumed due to the reduction in cold temperatures/snow/ice/hail etc. due to climate change | No further action | Risk to transport from high and low temperatures, high winds, lightning
STR6 | Asset | Structures | Moving bridges | Extreme hot days | Direct | Inability of the moving structure to articulate under high temperatures resulting in serviceability impacts. This can increase safety and performance risks and impacts | Whole country | Professional Head of Structures | Intervention dictated by Structural Asset Management Plans | Most of the assets within this category are classed as 'major structures' for example swing bridges. Significant capital investment is required and in current control periods deemed unaffordable. A sustainable approach has been to identify routine maintenance activities to keep the asset functional. These do not meet all stakeholder requirements | 6/moderate | Medium | Based on past asset failures | 6/moderate | 9/moderate | Medium | This risk comes to its own on swing bridges where components are unable to align under extremely hot conditions, thereby impacting on the short-term performance of the structure. Actions to manage this incident is covered in the asset's bespoke asset management plans as a BAU activity. The asset management plan does not currently include climate projections, but the long term action will be to replace the assets on the balance of cost and benefit | For major structures, these are covered in their own bespoke Asset Management Plans. For other structures, condition managed through route examination processes | Risk to transport from high and low temperatures, high winds, lightning
STR7 | Asset | Structures | Bridges, culverts and retaining walls | Erosion | Direct | Scour/undermining of structure | Whole country | Professional Head of Structures/Geotechnical | Risk consequence tools under development, triggers yet to be determined | Undermining of structure leading to loss of support and potentially fouling gauge. There is also the risk of loss of support of earthwork bearing track formation | 9/moderate | Medium | Based on past assets failures | 9/moderate | 12/major | Medium | It is expected that all critical retaining walls would be risk assessed against the consequence tools and necessary policy on intervention developed. However as this uses an unadapted policy the risk will rise | Assume current funding remains for current management practices | Risks to infrastructure services from river, surface water and groundwater flooding
T&RS1 | Asset | T&RS | Mobile plant, rail vehicle - rolling stock | Erosion | Interdependency (them on us) | Derailment due to landslip | Whole country | Professional Head of Geotechnical | For operations of T&RS this will be based either on the trigger/threshold for the local civils teams based on the discovery of infrastructure that is at risk of slipping, or on the discovery of a landslip that has already occurred | There is a risk across the whole country of landslips following lengthy periods of rainfall | 12/major | Medium | We have had past incidents relating to landslips (see Watford September 2016), but there is an expectation that this risk is already being managed by our Civils teams | 12/major | 16/major | Low | Increasing intense rainfall and lack of investment in drainage assets will increase the risk of failure in the future | We have low confidence in the risk rating but we have high confidence that the risk will increase in the absence of action | Risks to infrastructure services from river, surface water and groundwater flooding
T&RS10 | Asset | T&RS | Mobile plant, rail vehicle - rolling stock | Heavy rain/cloudburst | Direct | Water ingress into electrical equipment | Whole country | Head of T&RS | Evidence of water damage to electrical systems | There is a risk across the country of this occurring | 6/moderate | Medium | Current asset is well known and there are maintenance procedures in place to replace seals, etc. to mitigate this hazard. As T&RS assets have a life of c.30 years, the effect on future assets in unknown | 6/moderate | 6/moderate | Low | Increase in rainfall would increase the likelihood of failure of electrical equipment through water damage if electrical equipment design fails to take into account the hazard | Assumption that current assets have been replaced by 2050, and that weather resilience has been considered as part of the procurement of new assets | Risks to infrastructure services from river, surface water and groundwater flooding
T&RS11 | Asset | T&RS | Mobile plant, rail vehicle - rolling stock | Long hot, dry summer | Direct | Pollen and dust particles in cooling systems | Whole country | Head of T&RS | Series of failures of on board systems linked to clogging of filters | Greater risk of this occurring in Southern areas of the country where the temperatures historically are higher. Greatest risk in rural areas. Such failures have not been found on our fleets but have occurred on several diesel powered fleets | 3/minor | Medium | Current asset is well known, as these failures have occurred on DMUs in recent years we are aware of the hazard and manage fleets accordingly | 4/moderate | 4/moderate | Medium | Increase in temperatures and dry days will increase the likelihood of high pollen levels in the summer months. The outputs of the industry de-carbonisation strategy however will probably bring a reduction in diesel vehicles in future years. | Assumption that current assets have been replaced by 2050, and that weather resilience has been considered as part of the procurement of new assets | Risk to transport from high and low temperatures, high winds, lightning
T&RS12 | Asset | T&RS | Mobile plant, rail vehicle - rolling stock | Heat wave | Direct | Vehicle shut downs due to temperature sensor settings | Whole country | Head of T&RS | Series of vehicle shutdowns due to overheating | According to our fleet teams, the setting of temperature sensors in OTMs can be quite arbitrary (such as hottest day of year +10oC), with an increase in temperatures there will be a greater emphasis on cooling systems being able to cope with high temperatures. Greater risk of this occurring in Southern areas of the country where the temperatures historically are higher | 3/minor | Low | Point was raised as a risk with current fleet, no clear view on how this will be managed with future procurements. The current draft of the Key Trains Requirement (Rail Delivery Group owned, cross industry working group aiming to improve rail vehicle specifications) guidance document refers to the use of BS EN 50125-1:2014's temperature parameters as a general solution to setting operating temperature envelopes though it has been noted that just increasing the temperature envelope for equipment increases costs significantly | 4/moderate | 4/moderate | Low | Low confidence in this due to the following points: - current process has been described as fairly arbitrary - Weather resilience wording in the Key Trains Requirement guidance document is yet to be defined - Lack of clarity on the propulsion systems being considered for 2050 & 2080 | Increase of average temperatures and number of hot summer days offset by change in propulsion systems to meet decarbonisation targets & current work being done by the industry (see KTR) to set guidance for weather resilience | Risk to transport from high and low temperatures, high winds, lightning
T&RS13 | Asset | T&RS | On track machines | Long hot, dry summer | Direct | Reduced visibility for drivers passing a tamping site in summer months due to dust generation | Whole country | Head of T&RS | Driver reports of reduced visibility whilst passing tamping activities | Hazard raised by SCO Fleet Engineering Management as a current hazard when tamping in hot, dry conditions | 6/moderate | Medium | Greatest risk perceived to be the lack of visibility of track workers involved in tamping operations of inability to read signals | 9/moderate | 9/moderate | Medium | Current methodology for tamping is well known, perceived increase risk due to expected average temperature increases | No change in tamping methodology | Risk to transport from high and low temperatures, high winds, lightning
T&RS14 | Asset | T&RS | Rail vehicle - rolling stock | Snow/ice | Direct | Rheostatic banks filling with powder snow | Southern Scotland | Head of T&RS | Vehicle failures due to snow ingress into electrical equipment | Linked with Southern Scotland due it being at the greatest risk because of temperatures and number of operations, but credible for the entire country | 2/minor | Medium | Hazard is well known in vehicle design, so such a hazard is usually eliminated by design | 3/minor | 3/minor | High | Known potential hazard which is considered as part of electrical design. Increase in likelihood due to expected precipitation increase in future decades, thus increasing the risk of heavy snowfall in Scotland | No negative impact on resilience to snowfall in future rail vehicle designs for electrical equipment | Risk to transport from high and low temperatures, high winds, lightning
T&RS15 | Asset | T&RS | Rail vehicle - rolling stock | Flooding | Indirect | Impact on vehicles due to flooding at stabling locations | Whole country | Professional Head of Geotechnical | Evidence of localised flooding in stabling areas | Mainly linked to west coast areas or stabling areas on a flood plain due to either the amount of rain they see or due to the inherent risk of the stabling area flooding | 6/moderate | Medium | We have had several flooding instances on the network flooding over the last few years so there is a perceivable risk of this occurring. The impact however would mainly be operational either the flooding would disable the vehicles (such as due to damage to the electrical systems) or operationally the vehicles will not be able to be moved if the water is above the rail head (see GE/RT 8000 - M3 iss.2) | 6/moderate | 8/moderate | High | High confidence due to low likelihood of operating rules for flooded areas changing and low likelihood of vehicle failure modes due to floods changing | No fundamental change in the operation of rail vehicles in flooded areas | Risks to infrastructure services from river, surface water and groundwater flooding
T&RS16 | Asset | T&RS | Rail vehicle - rolling stock | High winds | Direct | Rail vehicle impact with flying objects due to high winds | Whole country | Head of T&RS | Wind speeds reached that enforce reduced speed operation or stopping of services in extreme scenarios | Linked to areas that are exposed to high winds, so potentially more a risk for the West Coast of the country than the East Coast. Risk will be greatest where the area also has significant amounts of vegetation | 4/moderate | Medium | ARP risk selected due it best suiting the various potential scenarios. There is a possibility that a flying object could penetrate a part of the vehicle and cause fatalities but the greatest numbers of scenarios will cause minor damage to vehicles. Either way the ARP risk is consistent at the level in column M | 6/moderate | 8/moderate | Medium | Hazard is reasonably well known and accounted for in vehicle design (see GM/RT 2100 iss.6 appendices for missile testing and BS EN 15152:2019) | Assumption that no further mitigation is put in place to mitigate these hazards | Risk to transport from high and low temperatures, high winds, lightning
T&RS17 | Asset | T&RS | Rail vehicle - rolling stock | Long hot, dry summer | Direct | Lineside fires due to rail grinding sparks | Whole country | Head of T&RS | Reports of lineside fires due to grinding operations | Risk is prevalent in the South where temperatures are higher but hazard can be encountered across the country when there has been hot & dry weather | 4/moderate | High | Known hazard for grinding activities, common occurrence but generally limited damage to infrastructure | 5/moderate | 6/moderate | Medium | Known potential hazard which is considered as part of electrical design. Increase in likelihood due to expected increase in number of hot days in future decade | Assumption that no further mitigation is put in place to mitigate these hazards | Risk to transport from high and low temperatures, high winds, lightning
T&RS18 | Asset | T&RS | Rail vehicle - rolling stock | Snow/ice | Direct | Freezing brakes in winter | Whole country | Head of T&RS | Reports of frozen brakes on vehicles in winter months | Drier systems are not powerful enough on our MPV fleet to de-ice brake systems. Also a problem for Stone blowers. Risk prevalent in Scotland due to colder winters | 3/minor | High | Common issue, but consequences are very minor (i.e. no shifts have been lost due to it) | 3/minor | 2/minor | Medium | Expectation that the frequency of this occurring will reduce as average winter temperatures rise | Assumption that no further mitigation is put in place to mitigate these hazards | Risk to transport from high and low temperatures, high winds, lightning
T&RS19 | Asset | T&RS | Rail vehicle - rolling stock | High winds | Indirect | Vehicle derailment due to vegetation obstruction on the line | Whole country | Local maintenance teams? | Not really applicable to T&RS, the decision threshold here is more in relation to when lineside vegetation should be regarded as precarious and removed. The only T&RS element is the decision to run/not run trains based on recorded wind speeds | See 'decision threshold' column. For previous incidents involving Network Rail fleets, refer to RAIB report 01/2018 and Kingswood runaway from 2006 | 12/major | Medium | We have had two incidents in the last 13 years of MPVs running away due to brake releases, the Markinch episode being due to the train striking vegetation on the line. Unbraked, out of control vehicle could cause multiple fatalities (level crossings, track workers, etc) | 12/major | 12/major | Medium | Following the Markinch runaway, action was taken to avoid a similar failure of the braking system. It can however be expected that the number of storms leading to large amounts of vegetation on the line will increase due to climate change over the coming years | Numbers of storms increases over the coming decades | Risk to transport from high and low temperatures, high winds, lightning
T&RS2 | Asset | T&RS | Rail vehicle - rolling stock | Heavy rain/cloudburst | Direct | Build up of water in the pantograph well of the unit | Whole country | Head of T&RS | Failure of unit due to build up of water in the pantograph well | History of this type of failure occurring in coastal locations, but possible to recreate a similar failure mode with high levels of rainfall | 3/minor | High | Known hazard for some EMUs, no incidents of this type known to have occurred on 313121. Worth considering as this could be a hazard for fleets we bring in over the coming years | 3/minor | 6/moderate | High | See column M, not a known hazard for 313121 but a credible hazard for T&RS in general, worth bearing in mind should Network Rail acquire further EMUs in future | That rolling stock portfolio continues to contain units that carry the risk | Risks to infrastructure services from river, surface water and groundwater flooding
T&RS20 | Asset | T&RS | Mobile plant, rail vehicle - rolling stock | Heat wave | Direct | Traction Motor Failure | Whole country | Head of T&RS | Series of failures linked to excessive operating temperature for traction motors | Greater risk of this occurring in Southern areas of the country where the temperatures historically are higher, increased risk for DC motors | 2/minor | Medium | Expected to see a phasing out of vehicles with DC traction motors over the next few years, the level of reliability of AC motors of future vehicles in such conditions is unknown | 2/minor | 4/moderate | Low | Increase in temperatures will increase the risk of overheating of traction motors, this is offset by the reduction in the number of vehicles fitted with DC traction motors running on our infrastructure | Assumption based on current working practices not changing | Risk to transport from high and low temperatures, high winds, lightning
T&RS3 | Asset | T&RS | Rail vehicle - rolling stock | High winds | Direct | Build up of water in the pantograph well of the unit | Coastal | Head of T&RS | Failure of unit due to build up of water in the pantograph well | History of this type of failure occurring in coastal locations with high waves | 4/moderate | High | Known hazard for some EMUs, no incidents of this type known to have occurred on 313121. Worth considering as this could be a hazard for fleets we bring in over the coming years | 4/moderate | 8/moderate | High | See column M, not a known hazard for 313121 but a credible hazard for T&RS in general, worth bearing in mind should Network Rail acquire further EMUs in future | Current design does not change | Risk to transport from high and low temperatures, high winds, lightning
T&RS4 | Asset | T&RS | Mobile plant, rail vehicle - rolling stock | Extreme hot days | Indirect | Derailment due to track buckle | Whole country | Professional Head of Track | Ambient temperature - decision to operate or operate with PSRs based on NR/L2/TRK/001 mod.14 | There is a risk of track buckles over the entirety of the country above a certain ambient temperature | 10/major | Medium | Consequence of such an event happening would be catastrophic, but the likelihood of the event happening at present is relatively low given the current risk mitigations in place. Risk increase in future due to ambient thresholds for track buckles being met more regularly | 12/major | 15/major | Medium | Mitigations are already in place for this hazard (i.e. running with PSRs or not running services at all), but there is a likelihood that track buckles will increase as the number of hot days increases given climate projections | Assumption based on current working practices not changing | Risk to transport from high and low temperatures, high winds, lightning
T&RS5 | Asset | T&RS | Rail vehicle - rolling stock | Extreme hot days | Indirect | OLE dewirement due to sag in OLE from high temperatures | Whole country | Head of Contact Systems | Ambient temperature above a defined threshold triggers the use of PSRs based on OLE standard | Increased risk of dewirements in high temperatures due to sag in contact wires | 9/moderate | Medium | Current asset is known, but there is historic evidence of the hazard occurring in high temperatures | 9/moderate | 12/major | Medium | Consequence of hazard occurring will not change over time, but increase of number of hot days will increase likelihood. History of event occurring in previous years in hot weather (July 2019) | Assumption based on current working practices not changing | Risk to transport from high and low temperatures, high winds, lightning
T&RS6 | Asset | T&RS | Mobile plant, rail vehicle - rolling stock | Heat wave | Direct | Traction Motor Failure | Whole country | Head of T&RS | Series of failures linked to excessive operating temperature for traction motors | Greater risk of this occurring in Southern areas of the country where the temperatures historically are higher, increased risk for DC motors | 4/moderate | Medium | Expected to see a phasing out of vehicles with DC traction motors over the next few years, the level of reliability of AC motors of future vehicles in such conditions is unknown | 1/minor | 1/minor | Medium | Increase in temperatures will increase the risk of overheating of traction motors, this is offset by the reduction in the number of vehicles fitted with DC traction motors running on our infrastructure | Assumption based on current working practices not changing | Risk to transport from high and low temperatures, high winds, lightning
T&RS7 | Asset | T&RS | Mobile plant, rail vehicle - rolling stock | Extreme hot days | Direct | Diesel motor failure | Whole country | Head of T&RS | Series of failures linked to excessive operating temperature for diesel motors. Overheating alarm on vehicles | Greater risk of this occurring in Southern areas of the country where the temperatures historically are higher | 6/moderate | Medium | Current asset is well known and capable of withstanding a large variety of temperatures | 6/moderate | 6/moderate | Medium | High operating temperatures can lead to a diesel engine failure due to overheating. The risk is that the number of failures will increase as it is expected that the number of extreme hot days will increase in the future decades. This is however offset by the commitment of the rail industry to decarbonisation over the coming years which will likely lead to a reduction in the number of diesel powered vehicles on the network | Assumption that different operating parameters for operation are not selected for equipment (refer to BS EN 50125-1:2014 for the environmental condition classes for rolling stock) | Risk to transport from high and low temperatures, high winds, lightning
T&RS8 | Asset | T&RS | Mobile plant, rail vehicle - rolling stock | Extreme hot days | Direct | Failure of electrical equipment through degradation | Whole country | Head of T&RS | Series of failures linked to operation of electrical equipment in excessive operating temperatures | Greater risk of this occurring in Southern areas of the country where the temperatures historically are higher | 6/moderate | Medium | Current asset is well known and capable of withstanding a large variety of temperatures | 6/moderate | 6/moderate | Medium | Asset is well known, and has a 30 year lifecycle so it is highly unlikely to be used in 2050 or 2080. This therefore becomes an element to be considered in the procurement of a new asset, where attention should be given to the necessary operating parameters listed in BS EN 50125-1:2014 | Assumption that current assets have been replaced by 2050, and that weather resilience has been considered as part of the procurement of new assets | Risks to subterranean and surface infrastructure from subsidence
T&RS9 | Asset | T&RS | Mobile plant, rail vehicle - rolling stock | Heat wave | Direct | Hydraulic failure | Whole country | Head of T&RS | Series of hydraulic failures linked to operation in excessive operating temperatures | Greater risk of this occurring in Southern areas of the country where the temperatures historically are higher | 6/moderate | Medium | Current asset is well known and capable of withstanding a large variety of temperatures | 6/moderate | 6/moderate | High | Asset is well known, and has a 30 year lifecycle so it is highly unlikely to be used in 2050 or 2080. This therefore becomes an element to be considered in the procurement of a new asset, where attention should be given to the necessary operating parameters listed in BS EN 50125-1:2014 | Assumption that current assets have been replaced by 2050, and that weather resilience has been considered as part of the procurement of new assets | Risk to transport from high and low temperatures, high winds, lightning
TR1 | Asset | Track | Track and S&C (jointed) | Extreme hot days | Direct | Track buckles in jointed track (rail) | Whole country | Professional Head of Track | Rail temps exceeding 54 deg C will require speed restrictions to control risk | Historic evidence of buckle trends shows that jointed track is more likely to buckle than CWR | 9/moderate | High | Increase in track buckles as temperatures rise with a greater likelihood of buckling | 9/moderate | 12/major | Medium | Track buckles more prevalent on jointed track by 2050 with potential line blockages or severe speed restrictions imposed | Jointed track is less resilient to heat beyond 38 deg C air temp. Assuming that Routes have managed all deficiencies to meet compliant design limits. However if this assumption proves to be incorrect then the risk for 2050 and 2080 will increase further | Risk to transport from high and low temperatures, high winds, lightning
TR10 | Asset | Track | CWR | Long hot, dry summer | Direct | Track buckles in CWR (rail) | Whole country | Professional Head of Track | Rail Temps exceed 56 resulting in speed restrictions to control risk | Deterioration of track quality as a result of inability to undertake routine maintenance activities. Also increased risk of staff fatigue and risk of being struck by trains whilst undertaking hot weather patrolling duties | 9/moderate | High | Historic failures will increase due to impact of not being able to deliver work during this period | 9/moderate | 12/major | High | Reduction in track work for long periods causes a deterioration of track quality resulting in speed restrictions | Maintenance work routinely undertaken during summer is restricted above 32 deg C. Extended periods of hot and dry weather will affect ability to carry out maintenance resulting in track quality deterioration | Risk to transport from high and low temperatures, high winds, lightning
TR11 | Asset | Track | S&C | Large diurnal temperature range | Direct | Track buckles in S&C | Whole country | Professional Head of Track | S&C on timber layouts and of weaker constructions (such as switch diamonds) unable to withstand rail temps above 54 deg C | Increased risk of misalignments and buckling due to rapid thermal expansion stresses | 6/moderate | High | Large changes in temperature variation causing imbalance in rail stress with variation exceeding 30 deg C in hot and cold temps | 9/moderate | 12/major | Medium | Increased thermal expansion in legacy S&C components that are less resilient to heat expansion | Currently 15% of S&C is modern variant, but future projections results in less than 1/3rd of assets being modernised, thereby unable to withstand large increases in temp. Assuming that Routes have managed all deficiencies to meet compliant design limits. However if this assumption proves to be incorrect then the risk for 2050 and 2080 will increase further | Risk to transport from high and low temperatures, high winds, lightning
TR12 | Asset | Track | Track and S&C | Higher average temperature | Direct | Track buckles in S&C | Whole country | Professional Head of Track | S&C on timber layouts and of weaker constructions (such as switch diamonds) unable to withstand rail temps above 54 deg C | Increased risk of misalignments and buckling due to rapid thermal expansion stresses | 6/moderate | High | Increase in track buckles as temperatures rise with a greater likelihood of buckling especially in legacy S&C construction | 9/moderate | 12/major | High | Track buckling in legacy S&C sites which currently comprise 85% of network | Future S&C renewal projections means less than 1/3rd of assets will be modernised by 2050 and around 45% by 2080 creating differential expansion between S&C and adjacent plain line and weaknesses in S&C. Assuming that Routes have managed all deficiencies to meet compliant design limits. However if this assumption proves to be incorrect then the risk for 2050 and 2080 will increase further | Risk to transport from high and low temperatures, high winds, lightning
TR13 | Asset | Track | Track and S&C | Heavy rain/cloudburst | Indirect | Flooded tracks and destabilisation leading to poor ride quality and speed restrictions or line closure | Whole country | Professional Head of Track and Professional Head of Drainage and Off Track | Water exceeds rail head level causing trains to stop or travel at caution | Historic failures where track has flooded due to inability for drainage (natural or drainage system) to cope with rain or blocked/broken drains. Water exceeds rail level and stops or slows trains down | 6/moderate | High | Flooded track caused by weaknesses in drainage systems or lack of drainage system | 9/moderate | 12/major | High | Flooded track caused by weaknesses in drainage systems or lack of drainage system | Excess rain exceeds drainage capacity resulting in weakened track assets and exposure to increased risk | Risks to infrastructure services from river, surface water and groundwater flooding
TR14 | Asset | Track | Track and S&C | High average rainfall over several days | Indirect | Flooded tracks and destabilisation leading to poor ride quality and speed restrictions or line closure | Whole country | Professional Head of Track and Professional Head of Drainage and Off Track | Water exceeds rail head level causing trains to stop or travel at caution | Historic failures where track has flooded due to inability for drainage (natural or drainage system) to cope with rain or blocked/broken drains. Water exceeds rail level and stops or slows trains down | 6/moderate | High | Flooded track caused by weaknesses in drainage systems or lack of drainage system | 9/moderate | 12/major | High | Flooded track caused by weaknesses in drainage systems or lack of drainage system | Excess rain exceeds drainage capacity resulting in weakened track assets and exposure to increased risk | Risks to infrastructure services from river, surface water and groundwater flooding
TR15 | Asset | Track | Track and S&C | High soil moisture | Interdependency (us on them) | Destabilised track and poor track quality causing speed restrictions or line closure | Whole country | Professional Head of Geotechnical | Track misaligned or very rough top causing a rapid reduction in ride quality | Historic failures especially on clay or peat areas in South or East of England resulting in destabilised embankments and cuttings | 9/moderate | High | High Soil moisture causes weaknesses in embankment stability | 9/moderate | 12/major | High | High Soil moisture causes weaknesses in embankment stability | Effect on earthworks saturated by water resulting in weakening track causing damage to track and deteriorating track quality conditions | Risks to infrastructure services from river, surface water and groundwater flooding
TR16 | Asset | Track | Track and S&C | Low soil moisture | Interdependency (us on them) | Destabilised track and poor track quality causing speed restrictions or line closure | Whole country | Professional Head of Geotechnical | Track misaligned or very rough top causing a rapid reduction in ride quality | Historic failures especially on clay or peat areas in South or East of England resulting in destabilised embankments and cuttings | 9/moderate | High | Low Soil moisture causes prolonged instability in embankments especially if followed by heavy and sustained rainfall | 9/moderate | 12/major | High | Low Soil moisture causes prolonged instability in embankments especially if followed by heavy and sustained rainfall | Effect on earthworks due to dryness will cause shrinkage and deterioration in track quality and condition | Risk to transport from high and low temperatures, high winds, lightning
TR17 | Asset | Track | Track and S&C | Flooding | Interdependency (us on them) | Flooding causing destabilisation of earthworks or cuttings, for example wash-outs, resulting in poor track geometry condition | Whole country | Professional Head of Geotechnical and Professional Head of Drainage and Off Track | Water undermines track support system (e.g. embankment/cutting) | Historic failures in earthwork due to flooding which undermines the track condition resulting in speed restrictions or line closures | 6/moderate | High | Detrimental impact on embankment stability causing deterioration of track geometry | 9/moderate | 12/major | High | Detrimental impact on embankment stability causing deterioration of track geometry | Flooding near rivers, coastal areas or low lying land resulting in weakening track formation and causing wash-out increasing future risk due to rise in river and sea levels. Likely to cause extensive damage to track | Risks to infrastructure services from river, surface water and groundwater flooding
TR18 | Asset | Track | Track and S&C | Erosion | Interdependency (us on them) | Destabilised track and poor track quality causing speed restrictions or line closure | Whole country | Professional Head of Geotechnical | Track misaligned or very rough top from eroded embankment or cutting causing a rapid reduction in ride quality | Historic failures especially on embankments resulting in track becoming uneven from embankment subsidence | 9/moderate | High | This could either be from standard river or flood flows (could result in rapid or slow deterioration) | 9/moderate | 12/major | Medium | Weakness in embankment stability caused by erosion from rivers or flood flows which affects track quality | Effect on track stability expected to increase especially in Southern half of country (cuttings and embankments) | Risks to infrastructure services from river, surface water and groundwater flooding
TR19 | Asset | Track | Track and S&C | Storms | Indirect | Destabilised track and poor track quality causing speed restrictions or line closure | Whole country | Professional Head of Geotechnical and Professional Head of Drainage and Off Track | Storm water caused from rainfall exceeds rail head level causing trains to stop or travel at caution | Historic failures where track has flooded during stormy weather due to inability for drainage to cope with rain or blocked/broken drains. Water exceeds rail level and stops or slows trains down | 9/moderate | High | Flooded track causes weaknesses in drainage systems to arise and also affects embankment stability. A key risk in coastal areas and near rivers | 9/moderate | 12/major | Medium | Storms likely to cause excessive rainfall over short periods causing instability in embankments and affecting track condition | weaker embankments will make track formation less stable and degrade its condition | Risks to infrastructure services from river, surface water and groundwater flooding | Risk to transport from high and low temperatures, high winds, lightning
TR2 | Asset | Track | Track and S&C | Higher average temperature | Direct | Track buckles in jointed track (rail) | Whole country | Professional Head of Track | Rail temps exceeding 54 deg C will require speed restrictions to control risk | Historic evidence of buckle trends shows that jointed track is more likely to buckle than CWR | 9/moderate | High | Increase in track buckles as temperatures rise with a greater likelihood of buckling | 9/moderate | 12/major | Medium | Track buckles more prevalent on jointed track by 2050 with potential line blockages or severe speed restrictions imposed | Jointed track is less resilient to heat beyond 38 deg C air temp. Assuming that Routes have managed all deficiencies to meet compliant design limits. However if this assumption proves to be incorrect then the risk for 2050 and 2080 will increase further | Risk to transport from high and low temperatures, high winds, lightning
TR20 | Asset | S&C | S&C | Snow | Direct | Blocked points due to snow accumulation and failures | Whole country | Head of S&C | Switches overwhelmed by snow build up preventing operation of points | Historic failures from severe snow storms (2010 and 2018) causing points with or without points heating to freeze or to become compacted with snow or ice | 6/moderate | Medium | Snow levels have reduced hence frequency of events likely to drop | 9/moderate | 9/moderate | Medium | Snow levels further reduced hence frequency of events likely to drop although severity could be worse | Impact will worsen although frequency of events will reduce | Risk to transport from high and low temperatures, high winds, lightning
TR21 | Asset | S&C | S&C | Snow/ice | Direct | Blocked points due to snow and ice accumulation and failures | Whole country | Head of S&C | Switches overwhelmed by snow build up preventing operation of points | Historic failures from severe snow storms (2010 and 2018) causing points with or without points heating to freeze or to become compacted with snow or ice | 6/moderate | Medium | Snow levels have reduced hence frequency of events likely to drop | 9/moderate | 9/moderate | Low | Snow levels further reduced hence frequency of events likely to drop although severity could be worse | Impact will worsen although frequency of events will reduce | Risk to transport from high and low temperatures, high winds, lightning
TR22 | Asset | S&C | Points operating equipment | Extreme hot days | Direct | Loss of detection and POE failures from heat affected electrical components (e.g. points modules) | Whole country | Head of S&C | Electronic components fail due to early life failures or exceeding design threshold | Excessive heat causes components in lineside cabinets or equipment cases to heat up reducing life expectancy of electronic components through thermal stressing | 6/moderate | Medium | Historic failures will increase due to negative effect of thermal stressing on electronic components increasing degradation | 6/moderate | 9/moderate | Medium | Lineside equipment housings for points operating equipment and associated components likely to be affected by increases in temperature | Effect increases by 2080 due to projected temp increases and current design parameters | Risk to transport from high and low temperatures, high winds, lightning
TR23 | Asset | S&C | Points operating equipment | Large diurnal temperature range | Direct | Points failures from POE and ironwork losing detection and exceeding critical detection tolerance | Whole country | Head of S&C | Electronic components fail due to early life failures or exceeding design threshold | Rapid rise and drop in temperatures causing electronic components in lineside cabinets or equipment cases to experience thermal stressing and reducing life expectancy of electronic components | 6/moderate | Medium | Historic failures will increase due to negative effect of thermal stressing on electronic components increasing degradation | 6/moderate | 9/moderate | Medium | Electrical and electronic components especially on lineside furniture likely to be affected by thermal stresses which will shorten life of components | Effect increases by 2080 due to projected temp increases and current design parameters | Risk to transport from high and low temperatures, high winds, lightning
TR24 | Asset | S&C | Points operating equipment | Flooding | Indirect | POE suffers from water ingress due to flooding | Whole country | Professional Head of Drainage and Lineside | Deterioration of sealed components or long period of immersion in flood water causing water ingress and affecting electrical/mechanical components | This is a low risk currently as assets are sealed and generally not affected by floods, however due to the position of equipment next to track protection by raising is not always feasible and persistent flooding would inevitably result in component degradation and failure | 2/minor | Low | Limited number of failures due to water ingress however deterioration in sealed material could affect electrical and mechanical components within points operating equipment | 6/moderate | 6/moderate | Medium | Increased risk of flooding likely to cause more instances of component failure without enhancement in component designs or other mitigation | Expected increase in flooding on coastal areas, rivers and on level land or cuttings that is more prone to effects of flooding | Risks to infrastructure services from river, surface water and groundwater flooding
TR25 | Asset | Track | Track and S&C | Higher average temperature | Direct | lateral stability of track compromised by inadequate sleeper/bearer support on ballast | Whole country | Professional Head of Track | Associated with S&C, curvature in track and connections between different sleeper/bearer types | Current controls with ballast and lateral end restraints are effective | 2/minor | High | Current failures associated with deficiencies and not poor design | 6/moderate | 6/moderate | Medium | Increased heat likely to result in more lateral force transfer into sleepers and impact on timber sleepers/bearers that are not as resilient or heavy as concrete | Increased temperature especially in southern half of the network will be impacted where sleepers/bearers are of an older design or made from timber | Risk to transport from high and low temperatures, high winds, lightning
TR3 | Asset | Track | Track and S&C | Heat wave | Direct | Track buckles in jointed track (rail) | Whole country | Professional Head of Track | Rail temps exceeding 54 deg C will require speed restrictions to control risk | Historic evidence of buckle trends shows that jointed track is more likely to buckle than CWR | 9/moderate | High | Increase in track buckles as temperatures rise with a greater likelihood of buckling | 9/moderate | 12/major | Medium | Track buckles more prevalent on jointed track by 2050 with potential line blockages or severe speed restrictions imposed | Jointed track is less resilient to heat beyond 38 deg C air temp. Assuming that Routes have managed all deficiencies to meet compliant design limits. However if this assumption proves to be incorrect then the risk for 2050 and 2080 will increase further | Risk to transport from high and low temperatures, high winds, lightning
TR4 | Asset | Track | Track and S&C | Large diurnal temperature range | Direct | Track buckles in jointed track (rail) | Whole country | Professional Head of Track | Rapid rises in Rail temps due to diurnal change resulting in poor condition assets being exposed through expansion | Historic failures causing rapid expansion and contraction of metal rails causing destabilisation in rail stress if not adequately stressed | 9/moderate | High | Historic failures will increase due to change in temperature variation due to rail temps exceeding 53 deg C | 9/moderate | 12/major | Medium | Track buckles more prevalent on jointed track by 2050 with potential line blockages or severe speed restrictions imposed | Jointed track is less resilient to heat beyond 38 deg C air temp. Assuming that Routes have managed all deficiencies to meet compliant design limits. However if this assumption proves to be incorrect then the risk for 2050 and 2080 will increase further | Risk to transport from high and low temperatures, high winds, lightning
TR5 | Asset | Track | Track and S&C | Long hot, dry summer | Direct | Track buckles in jointed track (rail) | Whole country | Professional Head of Track | Rail temps exceeding 54 deg C will require speed restrictions to control risk | Historic failures from previous hot summers where we have experienced double figures in track buckles or high number of speed restrictions that have resulted in cancellations and severe train delays to passengers and freight | 9/moderate | High | Historic failures will increase due to impact of not being able to deliver work during this period | 9/moderate | 12/major | High | Track buckles more prevalent on jointed track by 2050 with potential line blockages or severe speed restrictions imposed | Jointed track is less resilient to heat beyond 38 deg C air temp. Assuming that Routes have managed all deficiencies to meet compliant design limits. However if this assumption proves to be incorrect then the risk for 2050 and 2080 will increase further | Risk to transport from high and low temperatures, high winds, lightning
TR6 | Asset | Track | Track and S&C (CWR) | Extreme hot days | Direct | Track buckles in CWR (rail) | Whole country | Professional Head of Track | Rail Temps exceed 56 resulting in speed restrictions to control risk | Fully stressed and undisturbed track is resilient to between 54 and 59 deg C, but more modern variants can withstand up to 64 deg C. Current network coverage of modern CWR is just over 30%. Risk of excessive heat causing more track buckles increasing derailment risk | 6/moderate | High | Increase in track buckles as temperatures rise with a greater likelihood of buckling especially in legacy CWR construction | 9/moderate | 12/major | High | Track buckling in legacy CWR sites which currently comprise 60% of network | Legacy CWR track is resilient to 41 deg C air temp. Projected increases in modern CWR over next 30-50yrs means greater coverage over network. Assumes that Routes manage all deficiencies to meet compliant design limits. However if this assumption proves to be incorrect then the risk will increase | Risk to transport from high and low temperatures, high winds, lightning
TR7 | Asset | Track | Track and S&C | Higher average temperature | Direct | Track buckles in CWR (rail) | Higher average temperature | Professional Head of Track | Rail Temps exceed 56 resulting in speed restrictions to control risk | Fully stressed and undisturbed track is resilient to between 54 and 59 deg C, but more modern variants can withstand up to 64 deg C. Current network coverage of modern CWR is just over 30%. Higher than normal heat increases track buckles leading to derailment | 6/moderate | High | Increase in track buckles as temperatures rise with a greater likelihood of buckling especially in legacy CWR construction | 9/moderate | 12/major | High | Track buckling in legacy CWR sites which currently comprise 60% of network | Legacy CWR track is resilient to 41 deg C air temp. Projected increases in modern CWR over next 30-50yrs means greater coverage over network. Assumes that Routes manage all deficiencies to meet compliant design limits. However if this assumption proves to be incorrect then the risk will increase | Risk to transport from high and low temperatures, high winds, lightning
TR8 | Asset | Track | Track and S&C | Heat wave | Direct | Track buckles in CWR (rail) | Whole country | Professional Head of Track | Rail Temps exceed 56 resulting in speed restrictions to control risk | Fully stressed and undisturbed track is resilient to between 54 and 59 deg C, but more modern variants can withstand up to 64 deg C. Current network coverage of modern CWR is just over 30%. Persistent heat over long periods increases risk of track quality deterioration and buckling | 9/moderate | High | Increase in track buckles as temperatures rise with a greater likelihood of buckling especially in legacy CWR construction | 9/moderate | 12/major | High | Track buckling in legacy CWR sites which currently comprise 60% of network | Legacy CWR track is resilient to 41 deg C air temp. Projected increases in modern CWR over next 30-50yrs means greater coverage over network. Assumes that Routes manage all deficiencies to meet compliant design limits. However if this assumption proves to be incorrect then the risk will increase | Risk to transport from high and low temperatures, high winds, lightning
TR9 | Asset | Track | Track and S&C | Large diurnal temperature range | Direct | Track buckles in CWR (rail) | Whole country | Professional Head of Track | Rail Temps exceed 56 resulting in speed restrictions to control risk | Increased risk of rail breaks due to compressive stresses or track buckling as a result of disturbance or deficiencies | 6/moderate | High | Historic failures will increase due to change in temperature variation as a result of rail temps exceeding 56 deg C | 9/moderate | 12/major | Medium | Increased thermal expansion of rail in legacy components/assets | Legacy CWR track is resilient to 41 deg C air temp. Projected increases in modern CWR over next 30-50yrs means greater coverage over network. Assumes that Routes manage all deficiencies to meet compliant design limits. However if this assumption proves to be incorrect then the risk will increase | Risk to transport from high and low temperatures, high winds, lightning
Tun1 | Asset | Tunnels | Tunnels | Heat wave | Direct | Drying out of soil leading to change in loading to the extrados of the tunnel linings | Whole country | Professional Head of Mining and Tunnels | Intervention based on deteriorating condition against predetermined baseline requirements | More defects (loss of confinement of the arch/arch collapse), higher costs to repair, deterioration may lead to speed restrictions through tunnels Predominantly a risk to Tunnels through clay soils | 3/minor | Low | Limited information about soil/tunnel interaction. Minimal occurrences previously | 6/moderate | 9/moderate | Low | Low confidence as limited current information making future prediction harder | Assumptions based on how soils behave when saturated with water and how this would impact the tunnel lining | Risks to subterranean and surface infrastructure from subsidence
Tun2 | Asset | Tunnels | Tunnels | Snow/ice | Direct | Ice formation within shafts leading to risk to both operational trains and the workforce of falling ice | Whole country | Professional Head of Mining and Tunnels | Intervention based on Extreme Weather Plans determined by each route | Risk of tunnel closures to remove ice, thawing ice may fall and damage assets (OLE, Track), risk to safety of workforce Risk only to Tunnels with construction shafts | 12/major | High | Current issue for Tunnel operation. Likely to become less frequent but worse | 12/major | 12/major | Medium | Colder temperatures are becoming less prevalent. Isolated situations are likely to be more severe | Assumptions based on recurrent issue within tunnels which will occur more often with extended periods of low temperatures | Risk to transport from high and low temperatures, high winds, lightning
Tun3 | Asset | Tunnels | Tunnels | Snow/ice | Direct | Ice formation within the bores leading to prevention of trains operating within the tunnel | Whole country | Professional Head of Mining and Tunnels | Intervention based on Extreme Weather Plans determined by each route | Risk of tunnel closures to remove ice, teams required to enter tunnel more frequently to unblock tunnels, delays to morning trains while ice is removed | 12/major | High | Current issue for Tunnel operation. Likely to become less frequent but worse | 12/major | 12/major | Medium | Colder temperatures are becoming less prevalent. Isolated situations are likely to be more severe | Assumptions based on recurrent issue within tunnels which will occur more often with extended periods of low temperatures | Risk to transport from high and low temperatures, high winds, lightning
Tun4 | Asset | Tunnels | Tunnels | High average rainfall over season | Direct | Water ingress in tunnels leading to an increase in defects (e.g. open joints, spalling and missing bricks) as well as increase demand on track drainage | Whole country | Professional Head of Mining and Tunnels | Intervention based on deteriorating condition against predetermined baseline requirements | More defects, higher costs to repair, deterioration may lead to speed restrictions through tunnels. Drainage systems need improving to cope with additional flow Increase of Winter rainfall may destabilise hidden shafts and could lead to collapse in extreme cases | 12/major | Medium | Tunnel defects currently managed. Increase could make the level of defects unmanageable | 16/major | 20/severe | Medium | Medium confidence as there is uncertainty around whether current management practices will cope | Assumptions based on water ingress being a major cause of defects within tunnels. Assumed that increase Winter rainfall will increase water ingress in tunnels | Risks to infrastructure services from river, surface water and groundwater flooding
Tun5 | Asset | Tunnels | Tunnels | Flooding | Direct | Rising sea levels can lead to flooding to tunnels. These could result in scour to tunnels affecting their functionality | Coastal | Professional Head of Mining and Tunnels | Intervention based on increase in flood incidents in Tunnels | Tunnels could be closed due to flooding, TSRs in place in case of scour damage, closures could be lengthy if track bed is damaged by the flooding | 9/moderate | Medium | Few instances of flooding currently due to water levels therefore uncertain on total extent of damage | 12/major | 16/major | Medium | Medium confidence as limited current information making future prediction harder | Assumption based on increasing sea level resulting in tunnels being below tide levels and therefore flooding | Risks to infrastructure services from coastal flooding and erosion | Risk to offshore infrastructure from storms and high waves
Tun5A | Asset | Tunnels | Tunnels | Flooding | Direct | Increased river flows can lead to potential flooding to tunnels. These could result in scour to tunnels affecting their functionality | Whole country | Professional Head of Mining and Tunnels | Intervention based on increase in flood incidents in Tunnels | Tunnels could be closed due to flooding, TSRs in place in case of scour damage, closures could be lengthy if track bed is damaged by flooding | 9/moderate | Medium | Few instances of flooding currently due to water levels therefore uncertain on total extent of damage | 12/major | 16/major | Medium | Medium confidence as limited current information making future prediction harder | Assumption based on increasing river flows result in Tunnels being below water levels and therefore flooding | Risks to infrastructure services from river, surface water and groundwater flooding
Tun6 | Asset | Tunnels | Tunnels | High winds | Direct | High windspeed could dislodge signage within the tunnels leading to risk to workforce safety/or trains | Whole country | Professional Head of Mining and Tunnels | Intervention based on increase in occurrences reported | Increased specification for fixings and signage to cope with higher windspeeds. Potential restriction of access during high winds to carry out remedial work | 3/minor | High | Current risk low, would expect increase in risk only for significant wind speed increase | 6/moderate | 8/moderate | Low | Low confidence as limited current information making future prediction harder | Assumption based on increase in wind speed increasing pressure on signage and causing it to dislodge | Risk to transport from high and low temperatures, high winds, lightning
Tun7 | Asset | Tunnels | Tunnels | High soil moisture | Direct | Increased moisture content to soils below the tunnel can lead to swelling which can damage or cause heave to Tunnel Inverts | Whole country | Professional Head of Mining and Tunnels | Intervention based on deteriorating condition against predetermined baseline requirements | Tunnel closure could be required to repair defects below the track and within the drainage. Risk to train operations Predominantly a risk to Tunnels through clay soils | 6/moderate | Low | Minimal occurrences currently therefore unclear the impact this may have long term | 6/moderate | 9/moderate | Low | Low confidence as limited current information making future prediction harder | Assumptions based on how soils behave when saturated with water and how this would impact the tunnel lining | Risks to infrastructure services from river, surface water and groundwater flooding
Tun8 | Asset | Tunnels | Tunnels | Large diurnal temperature range | Direct | Increase in humidity leads to moisture being absorbed into masonry leading to spalling in combinations within the freeze thaw cycle | Whole country | Professional Head of Mining and Tunnels | Intervention based on deteriorating condition against predetermined baseline requirements | More defects, higher costs to repair | 12/major | Medium | Tunnel defects currently managed. Increase could make the level of defects unmanageable | 16/major | 20/severe | Low | Low confidence as limited current information makes future prediction harder and uncertainty around whether current management practices will cope | Assumptions based on this being a cause of defects within tunnels. Assumed that increase in humidity and temperature range will increase defects in tunnels | Risk to transport from high and low temperatures, high winds, lightning
VN1 | Asset | Vegetation | Trees | Long hot, dry summer | Direct | Potential increase in invasive non native infestations that affects the mortality in trees | Whole country | Professional Head of Drainage and Off Track | Trigger points dependant on condition measures applied to tree risk | Changes in climate more favourable to the spread of pathogens that have no known predation could lead to increased failure modes. The indicators would be captured during tree risk assessment. Potential for interventions to be increased to assess risk | 9/moderate | Medium | Infestations are likely to happen there will be uncertainty on the impact to the railway | 9/moderate | 9/moderate | Medium | Uncertainty with how accelerated pest and diseases will spread or what tolerances rates and management practices will be introduced to manage failures | With increased asset knowledge and further development of technologies to assist with location and condition data management, processes will be improved to apply proactive control. However, significant and rapid pest and disease outbreak may be unmanageable in view of the future climate projection
VN2 | Asset | Vegetation | Trees | Low soil moisture | Direct | Increase in tree mortality due to drought | Whole country | Professional Head of Drainage and Off Track | Trigger point can be related to long periods of drought during spring extending to early summer | Trees can be susceptible to pests and diseases following long periods of drought. In severe cases trees can die within 1 season. This increases tree risk failure | 9/moderate | Medium | Uncertainty whether this risk will have a noticeable affect on tree health within a short period of time or if this will be a contributing factor to changes in growth patterns over longer periods of time as tree adapt to local conditions | 9/moderate | 9/moderate | Low | Uncertain how trees will adapt to local conditions | There is no current data to assess trends and possible predictions | Risk to transport from high and low temperatures, high winds, lightning
VN3 | Asset | Vegetation | Trees/Bush | Long hot, dry summer | Direct | Increase in lineside fires | Whole country | Professional Head of Drainage and Off Track | Trigger point can be related to long periods of drought during spring extending to early summer | Lineside fires are likely to increase this can have an affect on performance and put operators at risk | 8/moderate | High | Likely to happen but impact would be minor where performance will be affected more than safety | 10/major | 10/major | High | Without any additional controls it is almost certain the occurrence of lineside fires and further service disruption will happen | There is no current data to assess trends and possible predictions, there are design features that can be adopted within new and existing woodlands and lineside habitats | Risk to transport from high and low temperatures, high winds, lightning
VN4 | Asset | Vegetation | Plants | Extended growth seasons (this is a combination of weather effects i.e. seasonal shift) | Direct | Longer growth seasons increasing encroachments | Whole country | Professional Head of Drainage and Off Track | Trigger points dependant on encroachments that require action and immediate action | Extended growth seasons and warmer wetter climates are likely to result in more rapid woody stem, leaf and bud development with conditions more favourable to exotic species | 3/minor | Medium | High confidence that growth seasons will increase but low confidence that this will result in growth rate increase and resulting encroachment increase | 5/moderate | 5/moderate | Medium | The negative effects of growth rate could be controlled by expected advances in management practices including more efficient inspection and maintenance technology. | There is no current data that suggests growth rate and subsequent encroachment rates are increasing, normalised or decreasing. If seasonal changes are expected vegetation and growth would be expected to adapt. Difficult to predict if this will be positive or negative to the railway
VN5 | Asset | Vegetation | Invasive plants | Extended growth seasons (this is a combination of weather effects i.e. seasonal shift) | Direct | Legislative challenges and increased risk to operatives dealing with plants | Whole country | Professional Head of Drainage and Off Track | Increase in financial penalties and claims, reputational damage and drain on resources to control spread | Extended growth season could increase the spread of invasive plants for established sites and new colonies to develop | 5/moderate | Medium | There is no specific data that suggests that invasive plants are adapting to current conditions more aggressively than native plants | 9/moderate | 9/moderate | Medium | Predictable that the range of non-native invasive plants will increase in the UK over the next 25 to 50 yrs. Their effects on the health of vegetation next to the railway is unknown | Likely that transport networks and corporate bodies will be a legislative and regulatory focus and vulnerable to claims
VN6 | Asset | Vegetation | Trees/leaf fall | Extended growth seasons (this is a combination of weather effects i.e. seasonal shift) | Indirect | Increased adhesion issues where unpredictable seasonal changes cannot be mitigated | Whole country | Professional Head of Drainage and Off Track | Adhesion performance indicators | Seasonal changes could lead to the effects of leaf fall being irregular leading to unexpected operational issues | 2/minor | Low | low confidence on the effects of seasonal changes and its level of change | 9/moderate | 9/moderate | Low | There no modelling currently in place that would suggest leaf fall and seasonal unpredictability will have impact on the railway | Seasonal performance will continue to be an industry focus, changes in vegetation composition, growth characteristics will require some understanding over the next 50 years
VN7 | Asset | Vegetation | Trees | Heavy rain/cloudburst | Direct | Washout resulting in loss of root anchorage | Whole country | Professional Head of Geotechnical | Increased incident/fault/condition indicators | This has links to earthwork and potential bank slip but also in locations next to the railway where substrates are washed out that were providing root anchorage | 9/moderate | Medium | Increase in storms would suggest that conditions that have the potential to cause soil washout will be more frequent | 9/moderate | 9/moderate | Low | Data is possibly available within the geotechnical community. There is no such data collection on failure due to washout currently | Future climate suggests storm events to be more frequent, if this continues the negative effects of washout are also likely to increase | Risks to infrastructure services from river, surface water and groundwater flooding | Risks to transport networks from slope and embankment failure
VN8 | Asset | Vegetation | Trees | Heavy rain/cloudburst | Direct | Waterlogging resulting in loss of root anchorage | Whole country | Professional Head of Drainage and Off Track | Increased incident/fault/condition indicators | This has links to drainage where trapped water or where areas are left to develop into wetland causes water log effect on trees and their roots | 9/moderate | Medium | Water logging around trees is known to result in tree death there is no current data or modelling in place for this type of defect | 9/moderate | 9/moderate | Low | No data that suggests that standing water or areas left to develop wetland is increasing and have negative effects on the railway | Without current modelling it is difficult to provide a high degree of confidence of the effects in the near future | Risks to infrastructure services from river, surface water and groundwater flooding
Note on T134: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Low temps is the nearest fit for ice, snow, hail etc.
Note on T135: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Low temps is the nearest fit for ice, snow, hail etc.
Note on T142: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The issue is mostly reduced rainfall, but this is not an option and high temperatures are a contributing factor.
Note on T151: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Low temps is the nearest fit for ice, snow, hail etc.
Note on T152: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Low temps is the nearest fit for ice, snow, hail etc.
Note on T160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The issue is mostly reduced rainfall, but this is not an option and high temperatures are a contributing factor.
Note on T167: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Low temps is the nearest fit for ice, snow, hail etc.
Note on T171: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Low temps is the nearest fit for ice, snow, hail etc.
Note on T177: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The issue is mostly reduced rainfall, but this is not an option and high temperatures are a contributing factor.
Note on T195: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The issue is mostly reduced rainfall, but this is not an option and high temperatures are a contributing factor.
Note on T218: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The issue is mostly reduced rainfall, but this is not an option and high temperatures are a contributing factor.
Note on T234: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The issue is mostly reduced rainfall, but this is not an option and high temperatures are a contributing factor.
Note on T268: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Low temps is the nearest fit for ice, snow, hail etc.
Note on T270: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Low temps is the nearest fit for ice, snow, hail etc.
Note on T271: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Low temps is the nearest fit for ice, snow, hail etc.
Note on T334: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The issue is mostly reduced rainfall, but this is not an option and high temperatures are a contributing factor.
Note on T349: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The issue is mostly reduced rainfall, but this is not an option and high temperatures are a contributing factor.
Note on T396: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A stretch as the issue is mostly reduced rainfall, but this is not an option and high temperatures are a contributing factor.
Note on T408: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A stretch as the issue is mostly reduced rainfall, but this is not an option and high temperatures are a contributing factor.
Note on T436: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Low temps is the nearest fit for ice, snow, hail etc.
Note on T463: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The issue is mostly reduced rainfall, but this is not an option and high temperatures are a contributing factor.
Note on T525: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The issue is mostly reduced rainfall, but this is not an option and high temperatures are a contributing factor.
Note on T553: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The issue is mostly reduced rainfall, but this is not an option and high temperatures are a contributing factor.

## CCRA3 risk list
Column1
CCRA3 Risks | Infra Risk
Risks to infrastructure networks (water, energy, transport, ITC) from cascading failures | I1
Risks to infrastructure services from river, surface water and groundwater flooding | I2
Risks to infrastructure services from coastal flooding and erosion | I3
Risks to bridges and pipelines from flooding and erosion | I4
Risks to transport networks from slope and embankment failure | I5
Risk to hydroelectric generation from low or high river flows | I6
Risks to subterranean and surface infrastructure from subsidence | I7
Risk to public water supplies from reduced water availability | I8
Risks to energy generation from reduced water availability | I9
Risks to energy from high and low temperatures, high wind, lightning | I10
Risk to offshore infrastructure from storms and high waves | I11
Risk to transport from high and low temperatures, high winds, lightning | I12
Risks to digital from high and low temperatures, high winds, lightning | I13

## PDA10 (hidden)
Risk | Start | 2050 | 2080 | Managed 2050 | Managed 2080
PD52 | 6/moderate | 6/moderate | 9/moderate | 6/moderate | 6/moderate | PD52, PD53
PD53 | 6/moderate | 6/moderate | 9/moderate | 6/moderate | 6/moderate
PD11 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate | PD11, PD15, PD16, PD63, PD86, PD192, PD193, PD196, PD198-200, PD202, PD205, PD206, PD245, PD246, PD249, PD251-253, PD255, PD258, PD259,
PD15 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD16 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD63 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD196 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD198 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD199 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD200 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD202 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD205 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD206 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD249 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD251 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD252 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD253 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD255 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD258 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD259 | 4/moderate | 4/moderate | 6/moderate | 4/moderate | 4/moderate
PD86 | 4/moderate | 4/moderate | 2/minor | 4/moderate | 4/moderate
PD192 | 4/moderate | 4/moderate | 2/minor | 4/moderate | 4/moderate
PD193 | 4/moderate | 4/moderate | 2/minor | 4/moderate | 4/moderate
PD245 | 4/moderate | 4/moderate | 2/minor | 4/moderate | 4/moderate
PD246 | 4/moderate | 4/moderate | 2/minor | 4/moderate | 4/moderate
PD100 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor | PD49, PD67, PD90, PD91, PD93, PD96, PD100, PD101, PD180, PD181, PD183, PD187, PD190, PD191, PD212, PD213, PD214, PD218, PD222, PD223, PD225, PD227, PD228, PD230, PD236, PD237, PD248, PD264, PD265, PD267, PD273-275, PD283, PD284, PD305
PD101 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD180 | 2/minor | 2/minor | 4/moderate | 2/minor | 2/minor
PD181 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD183 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD187 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD190 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD191 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD212 | 2/minor | 2/minor | 4/moderate | 2/minor | 2/minor
PD213 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD215 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD218 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD222 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD223 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD225 | 2/minor | 2/minor | 2/minor | 2/minor | 2/minor
PD227 | 2/minor | 2/minor | 4/moderate | 2/minor | 2/minor
PD228 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD230 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD236 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD237 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD248 | 2/minor | 2/minor | 4/moderate | 2/minor | 2/minor
PD264 | 2/minor | 2/minor | 4/moderate | 2/minor | 2/minor
PD265 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD267 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD273 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD274 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD275 | 3/minor | 3/minor | 6/moderate | 3/minor | 3/minor
PD283 | 2/minor | 3/minor | 4/moderate | 2/minor | 2/minor
PD284 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD305 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD49 | 3/minor | 3/minor | 6/moderate | 3/minor | 3/minor
PD67 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD90 | 2/minor | 2/minor | 4/moderate | 2/minor | 2/minor
PD91 | 3/minor | 3/minor | 6/moderate | 3/minor | 3/minor
PD93 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD96 | 2/minor | 2/minor | 3/minor | 2/minor | 2/minor
PD177 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor | PD87, PD177-179, PD207, PD210, PD211, PD224, PD226, PD260, PD262, PD263, PD285, PD290-292, PD299-301
PD178 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor
PD179 | 1/minor | 1/minor | 2/minor | 1/minor | 1/minor
PD207 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor
PD210 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor
PD211 | 1/minor | 1/minor | 2/minor | 1/minor | 1/minor
PD224 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor
PD226 | 1/minor | 1/minor | 2/minor | 1/minor | 1/minor
PD260 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor
PD262 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor
PD263 | 1/minor | 1/minor | 1/minor | 1/minor | 1/minor
PD285 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor
PD290 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor
PD291 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor
PD292 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor
PD299 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor
PD300 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor
PD301 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor
PD87 | 2/minor | 2/minor | 1/minor | 2/minor | 2/minor